## Sheet1
TANA WATER WORKS DEVELOPMENT AGENCY
KATHAGUTARI COMMUNITY BOREHOLE, EMBU COUNTY
TENDER NO: TWWDA/T/019/2022-2023 DRILLING, DEVELOPMENT AND TEST PUMPING OF 1NO. BOREHOLE
Item No. | Item Description | Units | Quantity | Rate (KSHS) | Amount (KSHS)
Bill No. 1 Preliminaries and General Items
Contractual Requirements
1.1 | Allow for provision of Performance security in accordance to the General conditions of contract | LS | 1
1.2 | Allow for provision of Insurances of works, workmen and third party in accordance with Clause 13 of the General Conditions of Contract | LS | 1
Contractor's mobilization and demobilization
1.3 | Mobilization, transportation of machinery and equipment to site and demobilization on completion | LS | 1
1.4 | Erecting and dismantling of contractor's borehole plant and equipment including but not limited to drilling unit, test pumping and borehole development unit, erection of camps and sanitary facilities | LS | 1
1.5 | Allow costs for providing water for all requirements of the contract | LS | 1
1.6 | Provide, erect and maintain standard TWWDA sign board at location shown by the Project Manager inclusive of removal and storage as directed by the Project Manager at end of maintenance period | LS | 1
| Sub Total for preliminaries and general items |  |  |  | 0
Item No. | Item Description | Units | Quantity | Rate (KSHS) | Amount (KSHS)
Bill N0. 2 | Borehole Works
2.1 | Drilling of borehole of minimum diameter 203 mm through all types of strata including disposal of excavated materials, taking any remedial measures to overcome caving-in or over drilling to accommodate sloughed material and collecting formation samples and prepare Geological logging chartsand keeping drilling records as specified between ground level and 100 meters below ground level | M | 100
2.2 | Ditto over 100m but not exceeding 200m ditto | M | 80
Supply and installation of screens and casings: Screens and casings shall be done to the satisfaction of the Project Manager. The base of the bottom casing shall be sealed as required
2.3 | Supply and install surface casings, mild steel 5 mm wall thickness, 153 mm internal diameter 4 m lengths | M | 4
2.4 | Supply and install 153 mm diameter plain steel casings pipes | M | 100
2.5 | Ditto but 153 mm diameter slotted steel casings in the borehole | M | 80
Item No. | Item Description | Units | Quantity | Rate | Amount
Gravel Pack
2.6 | Supply and install approved gravel pack (rounded 2-4 mm diameter). The rate to include for introduction of 500 g/m3 of calcium hypochlorite disinfectant | Ton | 22
Backfill above gravel pack
2.7 | Install approved backfill to 3 meters below ground level or as shall be directed by the Project Manager | M | 3
Borehole development
Development shall be done to the satisfaction of the Project Manager. Contractor shall propose methods he intends to use for approval. Rate to include installation and removal of necessary plant
Physical and chemical development of the borehole include inserting and removal of development equipment:
2.1 | (a) Physical Development | Hr | 24
2.11 | (b) Chemical Development | Hr | 8
Test pumping and recovery measurements
Rates to include for installation and removal of test pumping equipment
2.12 | Undertake Discharge Test as specified (24) hours for actual test pumping and 8 hours for insertion and removal of test pumping equipment | Hr | 32
2.13 | Undertake water level observation and record recovery | Hr | 8
WELL COMPLETION WORKS
2.14 | Allow costs for collecting water samples and carrying out full chemical and bacteriological analysis in an accredited laboratory approved by the Project officer and submission of full Borehole Competion Report | LS | 1
2.15 | Allow for Concreting of cover slab of 0.6mx0.6mx1.0m class 20/25 (1:2:4), Installation of bentonite/cement grout seal, fixing 6" borehole steel cap and engraving serial number | LS | 1
2.16 | Allow for making good surface reinstatement at the borehole to the satisfaction of the project officer | LS | 1
| Total Page 2 |  |  |  | 0
BILL SUMMARY
Total from Page 1 |  |  |  |  | 0
Total from Page 2 |  |  |  |  | 0
Sub-Total 1
Add 10% Contingencies ……………………………………………………………………..
Sub-Total 2
Add 16% VAT………………………………………………………………………………
Grand Total Taken to Form of Tender ……………………………………………………..