## SUMMARY
SUMMARY PAGE
CONSTRUCTION OF WATER TREATMENT WORKS AND REHABILITATION OF WATER SUPPLY PIPELINES FOR MWAI KIBAKI NATIONAL HOSPITAL - LEVEL VI (PRICES ARE INCLUSIVE OF 16% VAT)
ITEM | DESCRIPTION | AMOUNT
KES
1 | PRELIMINARIES AND GENERAL ITEMS
2 | DAYWORKS
3 | STILLING WELL, CHEMICAL DOSING CHANNEL AND FLOCCULATION CHANNEL
4 | SEDIMENTATION TANK
5 | FILTERS AND FILTER GALLERY
6 | 150M3 CLEAR WATER TANK
7 | PUMP HOUSE
8 | TREATED MAINLINE
9 | ELEVATED BACKWASH TANK
TOTAL
ADD 5% FOR CONTIGENCIES
GRAND TOTAL

## p&g
BILL No. 1
PRELIMINARIES AND GENERAL ITEMS
ITEM | DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
No. |  |  |  | (Kshs) | (Kshs)
1 | CONTRACTUAL REQUIREMENTS
1.1 | Allow for provision of Performance Security in accordance with the General conditions | Item | L.S
1.2 | Allow for provision of Insurance of Works and Contractor's Equipment, provision of Insurance against Accident to Workmen and provision of Third Party Insurance (including Employer's Property) all in accordance with the General Conditions of Contract. | Item | L.S
2 | SPECIAL REQUIREMENTS
2.1 | Contractor's Camp and Storage Yard: Allow for erection of the Contractor's Camp(s), Offices, Storage Yard and other facilities including mobilization, demobilization and movement of the works site on Completion. Include for all equipment, temporary measures, machines, tools, materials, facilities for workers, water and electricity supply etc. all as specified for execution of the Works, for the entire Contract Period. | Item | L.S
2.2 | Test Running of the Scheme: Allow for Test Running all the Project Components upon completion, for a period of 12 weeks upon completion and offical commissioning of the Works. Test Running to be carried out in close liaison with the Water Services Provider's Staff The Contractor to allow for 'on job' training of Operation and Maintenance Staff, Tools, Chemicals, etc, and ensure that the operations are carried out full time on a 24 hour basis. all in accordance with General and specific conditions | Item | L.S
2.3 | Allow for provision of Operation and Maintenance (O&M) Manuals in accordance with General and Specific Specifications of Bid Document | Item | L.S
2.4 | Allow for provision of As-Built Drawings in accordance with General and Specific Specifications of Bid Document | Item | L.S
PAGE TOTAL CARRIED FORWARD TO COLLECTION
3 | SPECIFIED REQUIREMENTS
Sign Boards
3.1 | Allow for provision, erection and maintenance of Project Sign Boards at the sites indicated by the Engineer's Representative, within the Project Area and in accordance with the Conditions of Contract. The rate quoted by the Contractor to include for payment of all statutory charges to the relevant Authority and removal after completion of the Project. | Nr | 1
3.2 | Allow a PC Sum of Ksh 50,000 for supply and installation of project plaque. Contractor to include for all requisite works associated with installation. | P.C | ITEM | 50000
3.3 | Add…% for profit, administration, attendance upon, overheads etc. for item 3.2 above. | %
4 | Material Testing
4.1 | Allow a P.C. sum of Ksh. 250,000 to be used for material testing, concrete testing, ground investigations, soil testing and other test as may be directed by the Engineer. | P.C | ITEM | 250000
5 | Setting Out & Survey Work
5.1 | Allow a Provisional Sum of Kshs. 100,000 for establishment of Level Survey Datum, Setting Out of the Works in accordance to the general conditions and any confirmatory survey works as required by the Engineer. | Item | P.C | 100000
The Setting Out / Survey Work including production of Survey Drawings to an agreed scale will be for the following Project Components:
i) Topographic Survey of Proposed Water Treatment Works Sites at 10m grid intervals including preparation of updated Layout Plan with contours at 0.5m interval,
ii) Engineering Survey of Treated Water Transmission Main including preparation of updated plan and profile, approximate length 4km
5.2 | Add 10% for profit, administration, attendance upon, overheads, etc. for Item 5.1 above. | %
6 | Supervision of Works
6.1 | Supervision: Allow a P.C. sum of Ksh. 400,000 for supervision of the works to be used as directed by the Engineer. | L.S | ITEM | 400000
6.2 | Allow a provisional PC sum of Ksh. 300,000 for provision of running and maintaining of supervision vehicle. | L.S | ITEM | 300000
6.3 | Add….% for profit, administration, attendance upon, overheads, etc for Items 6.1 and 6.2 above | %
PAGE TOTAL CARRIED FORWARD TO COLLECTION
7 | Relocation of Services
7.1 | Allow a P.C. Sum of Kshs. 250,000/ for Payments demanded by the Authorities for re location of existing services (water pipelines, power cable), Road crossings, etc., including any statutory levies to relevant Authorities. Liaison with the relevant Authorities shall be the responsibility of the Contractor for the timely execution of the Works. | Item | P.C | 250000
7.2 | Add 10% for profit, administration, attendance upon, overheads, etc. for Item 7.2 above. | %
8 | OTHER WORKS OBLIGATIONS
8.1 | Allow for any costs associated with compliance with Environmental, Health and Safety Requirements as specified in the Particular Specifications, the Environmental and Social Management and Monitoring Plan (ESMMP) as required by Government Agencies and Prevailing Legislation. | Item | L.S.
8.2 | Allow Ksh. 200,000 for branding of works as per the Engineers instruction and with TWWDA logo and colours | Item | L.S | 200000
PAGE TOTAL CARRIED TO COLLECTION
PRELIMINARIES SUMMARY
Collection 1
Collection 2
Collection 3
PRELIMINARIES BILL TOTAL CARRIED FORWARD TO SUMMARY PAGE

## Dayworks
BILL NO. 2: - DAYWORKS (INDICATIVE QUANTITIES)
ITEM | DESCRIPTION | Unit | QTY | RATE (KSHS) | AMOUNT (KSHS)
2.1 | THE WHOLE OF THIS BILL IS PROVISIONAL
LABOUR
The rates should include for all costs, such as insurance, travelling time, overtime, accommodation, use of small tools of trade, supervision, overheads and profit. Only time engaged upon work will be paid for:
2.1.1 | Unskilled labour | Hrs | 150
2.1.2 | Semi-skilled labour | Hrs | 50
2.1.3 | Skilled Labour | Hrs | 50
2.2 | PLANT
The rates should be included for all operational and maintenance costs, fuel, oil, operators, turn boys, Supervision, overhead and profits. Only the time employed on work will be paid for and the rates should include the idle, travelling and overtime.
2.2.1 | Compressor CP with 2 jacks | Hrs | 16
2.2.2 | Concrete vibrator (petrol or diesel) | Hrs | 48
2.2.3 | Portable water pump 50mp 50mm inclusive of hoses, couplings, valves and strainer) | Hrs | 32
2.3 | MATERIALS
2.3.1 | Ordinary Portland cement | tonne | 3
2.3.2 | Mild steel/High yield steel | tonne | 0.5
BILL NO.2 TOTAL CARRIED OVER TO SUMMARY PAGE

## stilling well
BILL NO. 2
KAHARO TREATMENT WORKS - STILLING WELL, CHEMICAL DOSING CHANNEL & FLOCCULATION BASIN
ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
No. |  |  |  | Kshs | KShs.
1 | GENERAL SITE CLEARANCE
1.1 | Clear site of all vegetation, including grubbing up roots, stripping the top soil and cart away arising material as directed by the Engineer | Ha. | 0.12
1.2 | Bulk Excavation (Provisional)
The following works shall be for general levelling of the site including benching and shall not be inclusive of the foundation trenches. Levels to be determined on site
1.2.1 | Excavate in normal soil depth n.e. 0.25m and dispose excavated material as directed by the Engineer | m2 | 1120
1.2.2 | Excavate,bench, haul, spread, water and compact suitable impermeable soil in layers not exceeding 150mm thick to achieve a MDD of 95% in areas specified by the Engineer. Contractor to identify and acquire the suitable impermeable soil approved by the Engineer on site in accordance to Drawing No. TWWDA/KWP/TWS-2 | m3 | 1398
1.2.3 | Spread top soil to slopping sides of site and plant approved grassing material. | m2 | 180
PAGE TOTAL CARRIED TO SECTION COLLECTION SHEET
2 | STILLING WELL
2.1 | Excavation
The rates shall include for all strutting, shuttering, stabilising the excavation faces and keeping the excavation free of water by pumping, bailing or other means.
Excavate for foundations, part backfill after construction and remainder, cart away to tips or use as fill on site, all as directed by the Engineer.
2.1.1 | Maximum depth n.e. 1.0 m | m3 | 7 |  |  | 16
2.1.2 | -Ditto - for depth 1 - 2 m | m3 | 4
2.1.3 | Extra over Item 1.1.1 & 1.1.2 for excavation in rock Class 'A', blasting not permitted (Provisional) | m3 | 1
2.1.4 | -Ditto- for excavation in rock Class 'B', blasting not permitted (Provisional) | m3 | 2
2.2 | Concrete Works
Provide, mix and place concrete as directed
2.2.1 | Plain concrete Class 15/20 in 75mm blinding layer under column bases | m2 | 6
Vibrated, reinforced concrete class 25/20 in:-
2.2.2 | Column bases | m3 | 3
2.2.3 | Columns | m3 | 1
2.2.4 | 200mm thick base slab | m3 | 3
2.2.5 | 200mm thick R.C walls | m3 | 10
2.2.6 | 150mm thick R.C baffle walls | m3 | 2
2.3 | Reinforcement
Provide and fix high tensile steel reinforcement to SRN 127 including cutting, bending, propping, with spacers and tying as specified.
2.3.1 | Reinforcement, all diameters | kg | 2280
2.4 | Formwork
Provide and fix shuttering including propping, strutting and striking all as specified
(i) Vertical Formwork - Class F1 Finish
2.4.1 | Vertical sides of Column bases, width n.e 0.4m | m | 20
(ii) Vertical Formwork - Class F3 Finish
2.4.2 | Vertical sides of Columns-width n.e 0.3m | m | 40
2.4.3 | Sides of 200mm thick base slab | m | 14
2.4.4 | Outer faces of stilling well walls-width n.e 3.8m | m2 | 52
2.4.5 | Inner faces of the stilling well walls-width n.e 3.8m | m2 | 46
2.4.6 | Sides of the baffle wall in stilling well | m2 | 16
(i) Horizontal Formwork - Class F1 Finish
2.4.7 | Soffit of Stilling Well Base Slab | m2 | 12
(i) Horizontal Formwork - Class F3 Finish
2.4.8 | Soffit of baffle wall in stilling well, width n.e 0.15m | m | 3
Other Formwork
2.4.9 | Boxing out for Pipes in 200mm thick R.C. Walls for Stilling Well pipe diameters n.e. 250mm and making good after pipe inserts installation. | Nr | 2
2.4.10 | Boxing out for Chemical dosing channel-1250mm x 800mm and making good after construction of chemical dosing channel | Nr | 1
2.5 | Concrete Surface Finish
2.5.1 | Provide Class UF3 Finish for top of base slab of stilling well | m2 | 12
2.6 | Construction Joints
Provide and install the following waterstops in construction joints including all surface treatment, formwork, forming of rebate 20mm x 20mm and sealing of rebate with polysulphide sealant all as per Drawings and Specifications.
2.6.1 | 200mm wide expandite super-cast water foil PVC or similar approved waterstop in construction joints in walls. | m | 28
2.7 | Metalwork
All steel work to be completely cleaned by acid dipping prior to galvanising.
2.7.1 | Provide and fix uPVC coated cast irons steps in stilling well as detailed in DRG No. TWWDA/KTW/FB-02 | Nr | 12
2.8 | Leak Proof Testing
2.8.1 | Allow for leak proof testing of Stilling Well as specified | Item | L.S
2.9 | Pipework Fittings & Valves
Supply, Transport to Site and Store in Secure Place Including Jointing Material, Bolts, Gaskets, Packing, Jointing Glue, etc, As Applicable
Raw Water Gravity Main Pipework - Approved Lined Ferrous Pipes
2.9.1 | 250mm dia. Flanged 900 bend with plain end beveled (Mark 1) | Nr | 1
2.9.2 | 250mm dia. Double flanged pipe with puddle flange at 400 mm from the flanged end,length 800mm (Mark 2) | Nr | 2
2.9.3 | 250mm dia. All flanged 900 bend (Mark 3) | Nr | 2
2.9.4 | 250mm dia. flanged spigot pipe 4500mm long (cut to suit on site) (Mark 4) | Nr | 1
2.9.5 | 250mm dia. flange adaptor (Mark 5) | Nr | 1
2.9.6 | 250mm dia. flanged spigot pipe 1200mm long (Mark 6) | Nr | 1
2.9.7 | 250mm dia. coupling (Mark 7) | Nr | 1
2.9.8 | 250mm dia. All flanged 900 Horizontal bend | Nr | 1
2.9.9 | 250mm double. flanged pipe 6000mm long (cut to suit on site for connection to existing upvc pipe) | Nr | 1
2.9.10 | 250mm Flanged Upvc to GI adaptor | Nr | 1
Scour Pipework - Approved Lined Ferrous Pipes
2.9.8 | 150mm dia. flanged spigot pipe 600mm long with puddle flange at 100mm from plain end (Mark i ) | Nr | 1
2.9.9 | 150mm dia all flanged 900 bend (Mark ii) | Nr | 2
2.9.10 | 150mm dia flanged spigot pipe cut to suit on site, length 950mm (Mark iii) | Nr | 1
2.9.11 | 150mm dia flanged adaptor (Mark iv) | Nr | 2
2.9.12 | 150mm Flanged spigot pipe cut to suit on site,length 1500 (Mark v) | Nr | 1
2.9.13 | 150mm dia Gate valve with extension spindle 1.2m long (short face) with a T-key for operation (Mark vi) | Nr | 1
2.9.14 | 150mm dia special flanged 900 bend with plain end beveled (mark vii) | Nr | 1
Transport From Site Store, Install, Test & Commission
Raw Water Gravity Main Pipework - Approved Lined Ferrous Pipes
2.9.15 | 250mm dia. Flanged 900 bend with plain end beveled (Mark 1) | Nr | 1
2.9.16 | 250mm dia. Double flanged pipe with puddle flange at 400 mm from the flanged end,length 800mm (Mark 2) | Nr | 2
2.9.17 | 250mm dia. All flanged 900 bend (Mark 3) | Nr | 2
2.9.18 | 250mm dia. flanged spigot pipe 4500mm long (cut to suit on site) (Mark 4) | Nr | 1
2.9.19 | 250mm dia. flange adaptor (Mark 5) | Nr | 1
2.9.20 | 250mm dia. flanged spigot pipe 1200mm long (Mark 6) | Nr | 1
2.9.21 | 250mm dia. coupling (Mark 7) | Nr | 1
2.9.8 | 250mm dia. All flanged 900 Horizontal bend | Nr | 1
2.9.9 | 250mm double. flanged pipe 6000mm long (cut to suit on site for connection to existing upvc pipe) | Nr | 1
2.9.10 | 250mm Flanged Upvc to GI adaptor | Nr | 1
Sour Pipework - Approved Lined Ferrous Pipes
2.9.22 | 150mm dia. flanged spigot pipe 600mm long with puddle flange at 100mm from plain end (Mark וֹ) | Nr | 1
2.9.23 | 150mm dia all flanged 900 bend (Mark וֹוֹ) | Nr | 2
2.9.24 | 150mm dia flanged spigot pipe cut to suit on site, length 800mm (Mark וֹוֹוֹ) | Nr | 1
2.9.25 | 150mm dia flanged adaptor (Mark וֹv) | Nr | 1
2.9.26 | 150mm Flanged spigot pipe cut to suit on site,length 1500 (Mark v) | Nr | 1
2.9.27 | 150mm dia Gate valve with extension spindle 1.2m long (short face) with a T-key for operation (Mark vוֹ) | Nr | 1
2.9.28 | 150mm dia special flanged 900 bend with plain end beveled (mark vii) | Nr | 1
PAGE TOTAL CARRIED TO SECTION COLLECTION SHEET
3 | CHEMICAL DOSING CHANNEL & DOSED WATER CHANNEL
3.1 | Concrete Works
Provide, mix and place concrete as directed
Vibrated Reinforced Concrete Class 25/20 in:-
3.1.2 | Base of channel | m3 | 3
3.1.3 | Walls of channel | m3 | 8
3.2 | Reinforcement
Provide and fix high tensile steel reinforcement to SRN 127 including cutting, bending,propping, with spacers and tying as specified.
3.2.1 | Reinforcement, all diameters | kg | 1320
3.3 | Formwork
Provide and fix shuttering including propping, strutting and striking all as specified.
(ii) Vertical Formwork - Class F3 Finish
3.3.1 | Sides of 200mm thick channel base slab | m | 17
3.3.2 | Walls of channel - width n.e. 0.1n | m | 42
3.3.3 | External walls of channel - width n.e. 2.0m | m2 | 24
3.3.4 | Internal walls of the channel - width n.e. 2.0m | m2 | 24
3.3.5 | Vertical sides of the wall-width n.e 0.3 | m | 1
3.3.6 | Ditto for-width n.e 0.2 | m | 1
Other Formwork
3.3.7 | Allow for 75mm x 75mm rebate in walls of dosed water channel for cover slabs. | m | 45
3.3.8 | Boxouts for Pipes in 200mm thick R.C. Walls for chemical dosing pipe diameter n.e 150 and making good after pipe inserts installation. | Nr | 1
3.4 | Concrete Surface Finish
3.4.1 | Provide Class UF3 Finish for top of base slab of channel | m2 | 13
3.5 | Construction Joints - Water Bar
Provide and install the following waterstops in construction joints including all surface treatment, formwork, forming of rebate 20mm x 20mm and sealing of rebate with polysulphide sealant all as per Drawings and Specifications
3.5.1 | 200mm wide expandite super-cast water foil PVC or similar approved waterstop in vertical construction joints in walls | m | 40
3.6 | Metal Work
All steelwork to be completely cleaned by acid dipping prior to galvanizing
3.6.1 | Provide and fix GMS open mesh cover with frame size 0.6m x 0.95m, to dosing channel, as per details on Drg. No. TWWDA/KTW/FB-01. Include for provision and fixing of fish tailed lugs into concrete walls. | Nr | 1
3.6.2 | Provide and fix GMS support bracket for GMS open mesh cover. Include for all materials (M.S. angle, plate, bolts, etc) and necessary drilling and fixing to concrete wall as required. | Nr | 1
3.6.3 | Provide and fix 900 mm high level balustrades of 40 mm diameter tubing Class B throughout, consisting of handrail and parallel middle rail 450 mm below the hand rail with balusters at maximum 1500 mm centres all as detailed on Drg. No. TWWDA/KTW/FB-02 | m | 28
3.6.4 | Provide and fix 750mm wide steel access staircase to chemical dosing channel as detailed on Drg. No. TWWDA/KTW/FB-01 and TWWDA/KTW/FB-02 | Nr | 1
3.7 | Miscellaneous
3.7.1 | Supply & fix Measuring Gauge as per details on Drg. No TWWDA/KTW/FB-04. | Nr | 1
3.7.2 | Supply & fix thin plate measuring weir as per details on Drg. No TWWDA/KTW/FB-04. | Nr | 1
3.8 | Precast Concrete Walkway Slabs
Precast concrete Class 25/20 finished fair on all surfaces and reinforced as shown on the drawings. Provide and fix:-
3.8.1 | 75mm thick cover slab size 950mm x 400mm wide including 2Nr. Mild steel key holes cast with slab constructed as per details on Drg. No. TWWDA/KTW/FB-04. for dosed water. channel | Nr | 32
PAGE TOTAL CARRIED TO SECTION COLLECTION SHEET
4 | FLOCCULATION BASIN
EARTHWORKS
4.1 | EXCAVATION
The rates shall include for all strutting, shuttering, stabilising the excavation faces and keeping the excavation free of water by pumping, bailing or other means.
Bulk excavations and top soil stripping for all structures are measured under (General Site Clearance)
Excavate below stripped level to formation level in common material, part backfill after construction and remainder, cart away to tips or use as fill on site, all as directed by the Engineer.
4.1.1 | Maximum depth n.e. 1.0 m | m3 | 23
4.1.2 | Ditto- but for scour chambers | m3 | 5
4.1.3 | Extra over Items 3.1.1 to 3.1.2 for excavation in rock Class 'A', blasting not permitted (Provisional) | m3 | 2
4.1.4 | -Ditto- for excavation in rock Class 'B', blasting not permitted (Provisional) | m3 | 3
4.1.5 | -Ditto- for excavation in rock Class 'C', blasting not permitted (Provisional) | m3 | 1.8
4.2 | FILL
4.2.1 | Transport approved excavated material from site stock pile and use as fill. Compact in 200mm thick layers,making up levels as directed by the Engineer. Compaction tests to be done for each layer as directed by the Engineer and to be included in the contractor's rates. | m3 | 161
4.2.2 | Provide, lay and level out the crushed stone, sand or gravel blinding 50mm thick to surface of filling, including watering and rolling to achieve satisfactory compaction. | m2 | 130
4.3 | CONCRETE WORKS
Provide, mix and place concrete as directed
4.3.1 | Plain concrete Class 15/20 in 75mm blinding layer under under retaining walls strip footing | m2 | 51
4.3.2 | Plain concrete Class 15/20 in 75mm blinding layer under base slab of the flocculation basin | m2 | 66
4.3.3 | Plain concrete Class 15/20 in 75mm blinding layer under scour chamber base. | m2 | 6
Vibrated, Reinforced concrete Class 25/20 in:-
4.3.4 | Retaining walls Strip footing | m3 | 21
4.3.5 | Flocculation basin base slab | m3 | 29
4.3.6 | Walls | m3 | 52
4.3.7 | Tie Beams | m3 | 1.8
Precast concreteclass 25/20 in:-
4.3.8 | Provide and fix precast concrete Baffle walls each150mm thick; 9.85m long ; depth ranging between 1.61m - 1.88m finished fair on all faces as detailed in drawing No. TWWDA/KTW/FB-03 | Nr | 8
4.3.9 | Ditto but 9.75m long ; depth ranging between 1.61m -1.68m | Nr | 9
4.4 | REINFORCEMENT
Provide and fix high tensile steel reinforcement to SRN 127 including cutting, bending, propping, with spacers and tying as specified.
4.4.1 | Reinforcement, all diameters | kg | 12525
4.5 | FORMWORK
Provide and fix shuttering including propping, strutting and striking all as specified
(i) Vertical Formwork - Class F1 Finish
4.5.1 | Sides of 400mm thick retaining wall footing | m | 82
4.5.2 | Sides of wall, width n.e 0.1m kicker | m | 85
4.5.3 | Walls below floor level | m2 | 169
4.5.4 | Inner faces of walls above floor level | m2 | 35
(ii) Vertical Formwork - Class F3 Finish
4.5.5 | Sides of 250mm thick sloping base slab - (1 in 45 slope) | m | 37
4.5.6 | Sides of walls-width n.e 0.1m kicker | m | 85
4.5.7 | Inner faces of walls above finished ground level | m2 | 44
4.5.8 | Walls above finished ground level | m2 | 67
4.5.9 | Tie beam width n.e 0.2 m | m | 25
(iii) Horizontal Formwork - Class F1 Finish
4.5.10 | Soffit of the tie beam-width n.e 0.75m | m | 12
(iv) Horizontal Formwork - Class F1 Finish
4.5.11 | Sloping sides of cantilever support for headstock | m2 | 1.2
(v) Other Formwork
4.5.12 | Boxouts for Pipes in 300mm thick R.C. Walls for scour pipe diameter n.e. 150mm and making good after pipe inserts installation | Nr | 2
4.5.13 | Boxouts for 600mm x 1000mm inlet control penstock in 300mm thick RC wall and making good after installation of the penstocks. | Nr | 2
4.5.14 | Boxouts for 600mm x 1300mm outlet control penstock in 300mm thick RC wall and making good after installation of the penstocks. | Nr | 2
4.6 | CONCRETE SURFACE FINISH
4.6.1 | Provide Class UF3 Finish for top of base slab of basin | m2 | 118
4.7 | CONSTRUCTION JOINTS
Provide and install the following waterstops in construction joints including all surface treatment, formwork forming of rebate and sealing of rebate with polysulphide sealant all as per Drawings and Specification.
4.7.1 | 200mm wide expandite super-cast water foil PVC or similar approved waterstop in construction joints in walls (Provisional) | m | 42
4.8 | LEAK PROOF TESTING
4.8.1 | Allow for leak proof testing of Flocculation Basin as specified | Item | L.S
4.9 | PIPEWORK, FITTINGS & VALVES
Supply, Transport to Site and Store in Secure Place including Jointing Material, Bolts, Gaskets, Packing, Jointing Glues, etc as Applicable.
4.9.1 | Special 600mm x 1000mm opening inlet control penstock with extended spindle and headstock (non-rising stem type) (Hambaker or approved equivalent). | Nr | 1
4.9.2 | Special 600mm x 1300mm opening outlet control penstock, non-rising stem type with extended spindle (Hambaker or approved equivalent) | Nr | 1
Sour Pipework - Approved Lined Ferrous Pipes
4.9.3 | 150mm dia. flanged spigot pipe 600mm long with puddle flange at 150mm from plain end (Mark h) | Nr | 1
4.9.4 | 150mm dia all flanged 90° bend (Mark i) | Nr | 2
4.9.5 | 150mm dia flanged spigot pipe cut to suit on site, length 1410mm (Mark j) | Nr | 1
4.9.6 | 150mm dia flanged adaptor (Mark k) | Nr | 4
4.9.7 | 150mm Flanged spigot pipe cut to suit on site,length 1750mm (Mark l) | Nr | 1
4.9.8 | 150mm dia Gate valve with extension spindle 1.2m long (short face) with a T-key for operation (Mark m) | Nr | 1
4.9.9 | 150mm dia flanged 90° bend with plain end bevelled (Mark n) | Nr | 2
4.9.10 | 150mm Flanged spigot pipe cut to suit on site,length 790mm (Mark o) | Nr | 1
Transport From Site Store, Install, Test and Commission
4.9.11 | Special 600mm x 1000mm opening inlet control penstock with extended spindle and headstock (non-rising stem type) (Hambaker or approved equivalent). | Nr | 2
4.9.12 | Special 600mm x 1300mm opening outlet control penstock, non-rising stem type with extended spindle (Hambaker or approved equivalent) | Nr | 2
Sour Pipework - Approved Lined Ferrous Pipes
4.9.13 | 150mm dia. flanged spigot pipe 600mm long with puddle flange at 150mm from plain end (Mark h) | Nr | 2
4.9.14 | 150mm dia all flanged 90 bend (Mark i) | Nr | 4
4.9.15 | 150mm dia flanged spigot pipe cut to suit on site, length 1410mm (Mark j) | Nr | 2
4.9.16 | 150mm dia flanged adaptor (Mark k) | Nr | 4
4.9.17 | 150mm Flanged spigot pipe cut to suit on site,length 1750mm (Mark l) | Nr | 1
4.9.18 | 150mm dia Gate valve with extension spindle 1.2m long (short face) with a T-key for operation (Mark m) | Nr | 2
4.9.19 | 150mm dia flanged 90° bend with plain end bevelled (Mark n) | Nr | 2
4.9.20 | 150mm Flanged spigot pipe cut to suit on site,length 790mm (Mark o) | Nr | 1
4.10 | Dosing Units
4.10.1 | Allow a PC sum of 100,000 for supply of Alum dosing unit together with alum delivery pipes and pipe conduits as specified by the engineer. | LS | 1 | 100000
4.10.2 | Install the alum dosing unit , delivery pipes and conduits for the alum dosing sytem and chlorine dosing system. | LS | 1
4.10 | MISCELLANEOUS
4.10.1 | Provide and apply Epoxy wall and floor coating, "MASTERTOP 1110T" or approved equivalent on internal surfaces of walls and floor of Flocculation Basin. | m2 | 199
4.11 | FLOCCULATED WATER CHANNEL
Concrete works
4.11.1 | Provide, mix and place concrete as directed
Vibrated, Reinforced concrete Class 25/20 in
4.11.2 | Walls | m3 | 2
4.11.3 | channel Slab | m3 | 4
4.12 | REINFORCEMENT
Provide and fix high tensile steel reinforcement to SRN 127 including cutting, bending, propping, with spacers and tying as specified
4.12.1 | Reinforcement, all diameters | kg | 750
4.13 | FORMWORK
Provide and fix shuttering including propping, strutting and striking all as specified
(i) Vertical Formwork - Class F1 Finish
4.13.1 | Sides of 200mm thick slab | m | 9
4.13.2 | walls width n.e 0.1m kicker | m | 8
4.13.3 | walls width n.e 1.6 m | m2 | 13
(ii) Vertical Formwork - Class F3 Finish
4.13.4 | walls width n.e 0.1m kicker | m | 7
4.13.5 | walls width n.e 1.6 m | m2 | 27
(iii) Horizontal Formwork - Class F1 Finish
4.13.6 | Soffit of flocculated water channel | m2 | 12
4.14 | CONCRETE SURFACE FINISH
| Provide Class UF3 Finish for top of base slab of flocculated water channel | m2 | 7
Metal Work
All steelwork to be completely cleaned by acid dipping prior to galvanizing
4.14.1 | Provide and fix GMS open mesh cover with frame size 1.475m x 1.25 m, to flocculated water channel as approved by the Engineer. Include for provision and fixing of fish tailed lugs into concrete walls. | Nr | 6
4.14.2 | Provide and fix 900 mm high level balustrades of 40 mm diameter tubing Class B throughout, consisting of handrail and parallel middle rail 450 mm below the hand rail with balusters at maximum 1500 mm centres all to Engineer's instructions | m | 20
Precast Concrete
Precast concrete Class 25/20 finished fair on all surfaces and reinforced as shown on the drawings. Provide and fix:-
4.14.3 | 75mm thick cover slab size 1250mm x 400mm wide including 2Nr. Mild steel key holes cast with slab constructed as per details on Drg. No. TWWDA/KTW/FB-04. for flocculated water channel | Nr | 11
4.15 | Scour Chamber Walling
Natural Stone Block Walling, Medium Chisel Dressed, Reinforced with 6mm dia. M.S. Reinforcement at Every Alternate Course, and Bedded, Jointed and Pointed in Cement Mortar (1:3):-
4.15.1 | 200 mm Walling | m2 | 12
4.15.2 | Provide all materials and Render the inside of Chamber Walls with 12.5mm thick Cement Mortar (1:3) | m2 | 10
4.16 | Site Protection works
| Provide, place and fill galvanised hexagonal double twist gabion boxes with rock size100-250mm fastened together on the embankment as directed by the Engineer. The gabion box 2m*1m*1m with a diaphram at the center with bracing wires at the centres both vertical and horizontal.Fastening wire shall be galvanised wire. | No | 60
PAGE TOTAL CARRIED TO SECTION COLLECTION SHEET
COLLECTION SHEET
STILLING WELL, CHEMICAL DOSING CHANNEL AND FLOCCULATION BASIN
Collection 1
Collection 2
Collection 3
Collection 4
TOTAL INCLUISVE OF V.A.T FOR STILLING WELL, CHEMICAL DOSING CHANNEL AND FLOCCULATION BASIN CARRIED TO SUMMARY PAGE

## sed tank
BILL No. 3
KAHARO TREATMENT WORKS - SEDIMENTATION TANKS - 2 Nr
ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
No. |  |  |  | (Kshs) | (Kshs)
1 | EXCAVATION
The rates shall include for all strutting, shuttering, stabilising the excavation faces, and keeping the excavation free of water by pumping, bailing or other means.
Bulk excavations and top soil stripping for all structures are measured under General Site Clearance
Excavate below stripped level to formation level in common material, part backfill after construction and remainder, cart away to tips or use as fill on site, all as directed by the Engineer.
1.1 | Maximum depth n.e. 1.0 m | m3 | 223
1.2 | -Ditto- but maximum depth 1.0 m to 2.0 m | m3 | 223
1.3 | -Ditto- but maximum depth 2.0 m to 3.0 m | m3 | 30.9
1.4 | -Ditto- but for the scour chamber | m3 | 8.5
1.5 | Trimming surface for blinding layer of concrete sloping 30 (6%) to horizontal | m2 | 163
1.6 | -Ditto- 9o (16%) to horizontal | m2 | 65
1.7 | Excavate trench for 150 mm dia. pipes in common material, trimming sides and preparing trench bottoms, backfill with approved hardcore and compact after laying of pipework depth n.e. 1.2 m. Note: Sections under Sedimentation Tank base slab shall be backfilled with Class 20/20 mass concrete surround, measured under Concrete Works. | m | 18.3
1.8 | Transport approved excavated material from site and use as fill and compact in 200 mm layers as specified on site as and where directed by the Engineer. Compaction tests to be done and rates to include for this. | m3 | 5.5
1.9 | Provide approved hardcore and compact in layers of 200mm, blinded with final material 25mm thick | m3 | 80
1.1 | Extra over Items 1.1 to 1.3 for excavation in rock Class 'A', blasting not permitted (Provisional) | m3 | 3
1.11 | -Ditto- for excavation in rock Class 'B', blasting not permitted (Provisional) | m3 | 51
1.12 | -Ditto- for excavation in rock Class 'C', blasting not permitted (Provisional) | m3 | 21
PAGE TOTAL CARRIED TO SECTION COLLECTION SHEET
2 | CONCRETE WORKS
Provide, mix and place concrete as directed
2.1 | Plain concrete Class 15/20 in 75 mm blinding layer under base slab of sedimentation tanks | m2 | 208
2.2 | Plain concrete Class 15/20 in 75 mm blinding layer under base slab of sludge collection sumps | m2 | 1.6
2.3 | Plain concrete Class 15/20 in 75 mm blinding layer under base slab of scour chamber | m2 | 4
2.4 | Plain concrete Class 20/20 in surround to 150 mm dia. sludge removal pipes | m3 | 7
Vibrated, Reinforced concrete Class 25/20 in
2.5 | 300 mm Base Slab - Sedimentation tank | m3 | 30
2.6 | 300 mm Base Slab - Sloping Slab - (6%) to horizontal | m3 | 34
2.7 | 300 mm Base Slab- Sloping Slab - (7%) to horizontal | m3 | 11
2.8 | 300 mm Base Slab - Sludge Collection Sumps | m3 | 1
2.9 | 300 mm Base Slab - Sludge Collection Channel | m3 | 7
2.1 | 200 mm Base Slab - Scour chamber | m3 | 1
2.11 | 200 mm Base Slab- Flocculated Water Channel | m3 | 4
2.12 | 200 mm Base Slab- Sedimentation Tank Inlet Channel | m3 | 2.5
2.13 | 200 mm Base slab - Walkways | m3 | 9
2.14 | 300 mm Walls - Sedimentation Tanks | m3 | 86
2.15 | 300 mm Walls - Sludge Collection Sumps | m3 | 1.5
2.16 | 300 mm Walls - Sludge Collection Channnel | m3 | 3.5
2.17 | 200 mm Walls - Scour chamber | m3 | 4
2.18 | 200 mm Walls - Flocculated Water Channel | m3 | 6
2.19 | 200 mm Walls - Sedimentation Tank Inlet Channel | m3 | 5.6
2.2 | Tie Beams | m3 | 4
2.21 | Cantilever platforms for Headstocks | m3 | 1
PAGE TOTAL CARRIED TO SECTION COLLECTION SHEET
3 | REINFORCEMENT
Provide and fix high tensile steel reinforcement to SRN 127 including cutting, bending, propping with spacers and tying as specified
3.1 | Reinforcement, all diameters | Kg | 29892
4 | FORMWORK
Provide and fix shuttering including propping, strutting and striking all as specified
(i) Vertical Formwork - Class F1 Finish
4.1 | Sides of 400 mm Base Slab - Sedimentation Tanks | m2 | 8
4.2 | Sides of 300 mm Base Slab - Sedimentation Tanks | m2 | 23
4.3 | Sides of 300 mm Base Slab - Sludge collection channel | m2 | 9.7
4.4 | Sides of 300 mm Base Slab - Sludge collection Sumps | m2 | 3
4.5 | Sides of 200 mm Base Slab - Scour chamber | m2 | 1.5
4.6 | Sides of 200 mm Base Slab - Flocculated Water Channel | m2 | 3.4
4.7 | Sides of 200 mm Base Slab - Inlet Water Channel | m2 | 3
4.8 | Sides of 200 mm Base Slab - Walkways | m2 | 45
4.9 | Sides of 200 mm Walls - Sump | m2 | 9
4.1 | Sides of 200 mm Walls - Sludge collection channel | m2 | 52
4.11 | Surfaces of walls, width 0.1 m kicker | m2 | 43
(i) Vertical Formwork - Class F2 Finish
4.12 | Sedimentation tank wall at expansion joints interface | m2 | 86
(iii) Vertical Formwork - Class F3 Finish
4.13 | Sides of Walls - Sedimentation Tank, width 0.3 m | m2 | 570
4.14 | Sides of Walls - Scour chamber, width 0.2 m | m2 | 33
4.15 | Sides of Walls - Flocculated Water Channel, width 0.2 m | m2 | 59
4.16 | Sides of Walls -Inlet Water Channel, width 0.2 m | m2 | 55
4.17 | Sides of cantilever supports for headstock | m2 | 1
4.18 | Sides of tie beams depth n.e. 0.6m | m2 | 26
(iii) Horizontal Formwork - Class F3 Finish
4.19 | Soffit of Flocuculated Water Channel, width 1.3m | m2 | 20
4.2 | Soffit of Inlet Water Channel, width 0.8m | m2 | 12
4.21 | Soffit of Walkways, width 0.9m - 1.3 m | m2 | 61
4.22 | Soffit of tie beams, width 0.45 m | m2 | 1
(v) Sloping Formwork - Class F3 Finish
4.23 | Sloping side of cantilever support for headstock | m2 | 1
Other Formwork- Class F3 Finish
4.24 | Box out for 400mm x 400mm square inlet control penstock in concrete walls and making good after installation of penstocks | Nr | 2
| Form 200 mm dia. cylindrical openings, 200 mm high, in base slab of inlet channel of sedimentation tank | Nr | 15
4.26 | Box out for 400mm x 200mm collection trough in concrete walls and making good after installation of troughs | Nr | 3
PAGE TOTAL CARRIED TO SECTION COLLECTION SHEET
5 | PRECAST CONCRETE SLABS
Precast concrete Class 25/20 finished fair on all surfaces and reinforced as shown on drawings. Provide and fix:
5.1 | 75mm thick cover slabs size 1250mm long x 400mm wide including 2 Nr. mild steel key holes cast with slab constructed as per details on Drg. No. TWWDA/KTW/ST-03 | Nr | 11
6 | CONCRETE SURFACE FINISH
6.1 | Provide Class UF3 Finish for top of base slab of Sedimentation Tanks, Channels, Walkways, etc. | m2 | 96 |  |  | 48
6.2 | Provide all materials and finish surface of concrete with cement mortar 1:4 to required slope in sludge concentration pockets | m2 | 28
7 | CONSTRUCTION JOINTS
Provide and install the following waterstops in construction joints including all surface treatment, formwork, forming of rebate 20 mm x 20 mm and sealing of rebate with polysulphide sealant all as per Drawings and Specification.
| 200 mm wide expandite super-cast waterfoil PVC or similar approved waterstop in vertical/horizontal construction joints in walls | m | 221
7.2 | Approved expansion board, thickness 25mm between sedimentation tank and settled water channel | m2 | 21
PAGE TOTAL CARRIED TO SECTION COLLECTION SHEET
8 | METAL WORK
All steelwork to be completely cleaned by acid dipping prior to galvanising.
Galvanised mild steel tubular balustrades all framed and welded together, including all necessary labours and fittings on tubings:
8.1 | Provide and fix 900 mm high level balustrades of 40 mm diameter tubing Class B throughout, consisting of handrail and parallel middle rail 450 mm below the hand rail with balusters at maximum 1500 mm centres | m | 100
8.2 | Provide and fix GMS settled water collection troughs length 4,000 mm made out of 6mm thick GMS sheet as detailed on Drg. No. TWWDA/KTW/ST-01 Include 6 mm thick galvanised steel plate welded to end of trough | Nr | 3
8.3 | Provide and fix 254 mm x 146 mm x 31 kg/m GMS universal beams 7,000 mm long. Include for all materials, bolts, etc., drilling and fixing into concrete as detailed on Drg. No. TWWDA/KTW/ST-01 | Nr | 1
8.4 | Provide and fix GMS support clamps including for all materials and necessary drilling and fixing to GMS universal beams or bracket as required. | Nr | 6
8.5 | Provide and fix 100 mm x 100 mm x 8 kg/m angle bracket 700mm long fixed to beam by means of 2 Nr 12 mm rawl bolts 100 mm long, include for all drilling. | Nr | 3
8.6 | Provide and fix 750 mm x 450 mm x 6 mm thick M.S. Plate welded to collection trough and fixed to wall of Sedimentation Tank with 20 mm dia., 150 mm long rawl bolts. Include for packing and sealing of joint between plate and wall. | Nr | 6
8.7 | Provide all materials and fix GMS CAT ladder, length 4.5m to inside of chamber as per detail Drg. No TWWDA/KTW/ST-03 | Nr | 1
8.8 | Provide and fix lockable G.M.S Open Mesh Flooring to scour chamber 1400 mm x 1500 mm | Nr | 2
8.9 | Ditto but for- flocculated channel outlet 1250 mm x 2300 mm | Nr | 1
9 | PAINTING AND DECORATING
Provide, prepare and apply one coat mordant solution, one undercoat and two coats gloss enamel paint on galvanised metal work externally on:
9.1 | Guardrail pipe and fittings including 900 mm high level balustrades | m | 65
9.2 | Decanting troughs | m2 | 37
9.3 | Exposed Pipework and fittings | Item | L.S
9.4 | Provide and apply 3 coats of approved epoxy paint on one coat epoxy primer to internal concrete surfaces of Sedimentation Tanks (water line only) ('Masterseal 180' as made by BASF or approved equivalent). | m2 | 284
10 | LEAK PROOF TESTING
10.1 | Allow for leakproof testing of all Sedimentation Tanks and flocculation water channel as specified | Item | L.S
PAGE TOTAL CARRIED TO SECTION COLLECTION SHEET
11 | PIPEWORK, FITTINGS & VALVES
Supply Transport to Site and Store in Secure Place
including Jointing Material, Bolts Gaskets, Packing, Jointing Glues, etc. as Applicable
11.1 | 400mm x 400mm square opening penstock non-rising stem type with extended spindle & head stock | Nr | 2
Scour Pipework - Approved Lined Ferrous Pipes to Class NP16
11.2 | 150mm dia. special single flanged 90° bend (Mark A) | Nr | 1
11.3 | 150mm dia. all flanged gate valve with extension spindle and wheel Euro 20 Series, type 23 or approved equivalent (Mark B) | Nr | 1
11.4 | 150mm dia. flanged spigot pipe, length 1200mm with puddle flange at 380 mm from spigot end (Mark C) | Nr | 1
11.5 | 150mm dia. Coupling (Mark D) | Nr | 2
11.6 | 150 mm dia. plain ended pipe length 4m with couplings (Mark E1) | Nr | 1
11.7 | Ditto- length 6m with couplings (Mark E2) | Nr | 1
11.8 | 150mm dia. plain ended pipe, length 1200mm with puddle flange at 155mm from one end (Mark F) | Nr | 1
Transport From Site Store, Install, Test and Commission
11.9 | 400mm x 400mm square opening penstock non-rising stem type with extended spindle & head stock (Ham baker or approved equivalent) | Nr | 2
Scour Pipework - Approved Lined Ferrous Pipes to Class NP16 as shown in Drg No. TWWDA/KTW/ST-03
11.1 | 150mm dia. single flanged 90° bend (Mark A) | Nr | 1
11.11 | 150mm dia. all flanged gate valve with extension spindle and wheel Euro 20 Series, type 23 or approved equivalent (Mark B) | Nr | 1
11.12 | 150mm dia. flanged spigot pipe, length 1200mm with puddle flange at 380 mm from spigot end (Mark C) | Nr | 1
11.13 | 150mm dia. Coupling (Mark D) | Nr | 2
11.14 | 150 mm dia. plain ended pipe length 4m with couplings (Mark E1) | Nr | 1
11.15 | Ditto- length 6m with couplings (Mark E2) | Nr | 1
11.16 | 150mm dia. plain ended pipe, length 1200mm with puddle flange at 155mm from one end (Mark F) | Nr | 1
PAGE TOTAL CARRIED TO SECTION COLLECTION SHEET
COLLECTION SHEET
SEDIMENTATION TANK
Collection 1
Collection 2
Collection 3
Collection 4
Collection 5
Collection 6
TOTAL INCLUSIVE OF V.A.T. FOR SEDIMENTATION TANK CARRIED TO SUMMARY PAGE

## filters
BILL NO. 4
KAHARO TREATMENT WORKS - FILTERS, FILTER GALLERY
ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
No. |  |  |  | Kshs | KShs.
1 | EXCAVATION
The rates shall include for all strutting, shuttering, stabilising the excavation faces, and keeping the excavation free of water by pumping, bailing or other means.
Bulk excavations and top soil stripping for all structures are measured under General Site Clearance
Excavate below stripped level to formation level in common material, part backfill after construction and remainder, cart away to tips or use as fill on site, all as directed by the Engineer.
1.1 | Maximum depth n.e. 1.0 m | m3 | 110
1.2 | -Ditto- but maximum depth 1.0 m to 2.0 m | m3 | 45
1.3 | -Ditto- but maximum depth 2.0 m to 3.0 m | m3 | 1
1.4 | Transport approved excavated materials from site and use as fill and compact in 200mm layers as specified on site as and where directed by the Engineer. | m3 | 4.5
1.5 | Provide approved hardcore and compact in layers of 200mm, blinded with final material 25mm thick | m3 | 34
1.6 | Extra over Items 1.1 to 1.3 for excavation in rock Class 'A', blasting not permitted (Provisional) | m3 | 9.4
1.7 | -Ditto- for excavation in rock Class 'B', blasting not permitted (Provisional) | m3 | 15
1.8 | -Ditto- for excavation in rock Class 'C', blasting not permitted (Provisional) | m3 | 12
PAGE TOTAL CARRIED TO SECTION COLLECTION SHEET
2 | CONCRETE WORKS
Provide, mix and place concrete as directed
Plain Concrete Class 15/20 in 75mm Blinding layer under
2.1 | Base slab for filters | m2 | 60
2.2 | Base slab for filter gallery | m2 | 23 |  |  | 11.5
2.3 | Base slab- Back wash water channel | m2 | 11
2.4 | Mass Concrete Class 15/20 between filter water collection channel end wall and filter gallery wall | m3 | 7.5
Vibrated Reinforced Concrete class 25/20 in:-
2.5 | Base slab - filter | m3 | 18
2.6 | Base slab - filter gallery | m3 | 7
2.7 | Wall - settled water channel / filter | m3 | 2.9
2.8 | Wall-settled water channel/sedimentation tank | m3 | 4.4
2.9 | Wall - filter / filter gallery | m3 | 12.3
2.1 | Side walls - filter | m3 | 36
2.11 | Base slab - settled water channel | m3 | 3
2.12 | Base slab - filter inlet channel | m3 | 1.1
2.13 | Wall - filter inlet channel | m3 | 2.5
2.14 | Cantilevered platforms for headstocks | m3 | 1
2.15 | Wall - filter water collecting channel | m3 | 3
2.16 | Walls - washwater overflow channel | m3 | 2.5
2.17 | Base - washwater channel | m3 | 4
2.18 | Walls - washwater collection trough | m3 | 1.5
2.19 | Base - washwater collection trough | m3 | 2.5
2.2 | Wall - filtered water channel | m3 | 3.3
2.21 | Top slab - filtered water channel | m3 | 1.7
2.22 | External wall - filter gallery | m3 | 1.7
2.23 | Walkway slabs | m3 | 1
2.24 | Ring Beams - ground floor | m3 | 1.7
PAGE TOTAL CARRIED TO SECTION COLLECTION SHEET
3 | REINFORCEMENT | [6 empty] | 3
Provide high tensile steel reinforcement to SRN 127 including cutting, propping, spacing and tying as specified
3.1 | All diameters | Kg | 13332
4 | FORMWORK
Provide and fix shuttering including propping, strutting and striking all as specified
Vertical Formwork - Class F1 Finish
4.1 | 300 mm side for base slab - filter | m | 21.1
4.2 | 300 mm side for base slab - filter gallery | m | 29
Vertical Formwork - Class F3 Finish
4.3 | 300 mm side for base slab - filter collection channels | m | 27
4.4 | Walls-filter collection channels -(0.3m-0.425m) | m | 27
4.5 | Walls-filter collection channels (0.3m-0.8) | m | 27
4.6 | Walls-Wash water channels -(0.3m-0.4m) | m | 9
Horizontal Formwork - Class F2 Finish
4.7 | Soffit of slab - inlet channel (0.6 m - 0.8 m) | m2 | 7
4.8 | Soffit of walkway slab (0.1 m - 0.3 m) | m2 | 4.2
4.9 | Soffit of slab-settled water channel (0.8m-1.0m) | m2 | 16
Vertical Formwork - F2 Finish
4.12 | Sides of walls - Filters/Filtered Water Channel, width 0.1 m | m | 64.4
4.13 | Ring beams (0.3 m - 0.6m) | m2 | 9.5
Vertical Formwork - F1 Finish
4.14 | External walls-settled water channel (1.0 m - 2.0 m) | m2 | 26
Vertical Formwork - F3 Finish
4.15 | Internal walls - settled water channel (1.0 m-2.0 m) | m2 | 22
Vertical Formwork - F3 Finish
4.16 | Wall - filter / filter gallery (4.5 m - 6.0 m) | m2 | 86
Vertical Formwork - F3 Finish
4.17 | Walls filter (3.4 m - 4.8 m) | m2 | 242
4.18 | Wall - inlet channel (1.0 m - 1.5 m) | m2 | 25
4.19 | Walls - filter collecting channel (0.5 m - 1.0 m) | m2 | 36
4.2 | Walls - filter gallery (1.5m-1.8m) | m2 | 5
4.21 | 150 mm side - walkways | m | 19
Sloping Formwork - F3 Finish
4..22 | Cantilevered platforms for headstocks (0.1 m - 0.3 m) | m | 1
Vertical Formwork - F3 Finish
4.23 | Cantilevered platforms for headstocks (0.1 m - 0.3 m) | m | 1
Horizontal Formwork - F3 Finish
4.24 | Soffit of washwater collection trough (0.8 m - 1.0 m) | m2 | 12
Vertical Formwork - F3 Finish
4.25 | Walls - washwater collection trough (0.4 m - 0.8 m) | m2 | 24
4.26 | Walls - filtered water channel (1.0 m - 1.5 m) | m2 | 44
Horizontal Formwork - F2 Finish
4.27 | Soffit of roof - filtered water channel (1.0 m - 1.5 m) | m2 | 11
PAGE TOTAL CARRIED TO SECTION COLLECTION SHEET
5 | CONSTRUCTION JOINTS
Provide and install the following waterstops in construction joints including all surface treatment, formwork, forming of rebate 20mm x 20mm and sealing of rebate with polysulphide sealant all as per Drawings and Specifications.
5.1 | 200 mm wide Expandite Supercast water foil PCV or similar approved waterstopin vertical /horizontal construction joints | m | 116
5.2 | Approved expansion board, thickness 25mm between sedimentation tank wall and settled water channel. | m2 | 14
6 | OPENINGS
6.1 | Form 200 mm diameter opening through 150 mm base by placing G.I. Pipe sleeve and removing after concreting for filter inlet channel | Nr | 4
7 | PROVIDE CLASS UF3 FINISH
7.1 | Provide all materials and lay cement screed (1:4) to required falls as indicated (Avg. 50mm thick ) in washwater channel | m2 | 8.9
7.2 | - Ditto - in filtered water channel | m2 | 11
Provide all materials and lay grano finish on cement screed in:-
7.3 | Filter gallery | m2 | 17
PAGE TOTAL CARRIED TO SECTION COLLECTION SHEET
8 | FILTER UNDER DRAINAGE SYSTEM
Concrete Class 25/20 precast concrete:
8.1 | Provide all materials and fix with approved sealer, filter under drain slabs 1600 mm long (in 3 pieces) x 700 mm wide x 75 mm thick as detailed on Drg. No. TWWDA/KTW/FFG-07. Include for bolt holes and casting in 100 mm diameter pipe with puddle flange as detailed in the drawing. Include reinforcement and G.S. nipple as detailed. | Nr | 6
8.2 | Supply and fix 16 mm diameter G.S. bolts and nuts as detailed on Drg. No. TTWDA/KTW/FFG-07. | Nr | 28
8.3 | - Ditto - 100 mm diameter G.I. socketted tee with 12 mm diameter GMS nut welded on top and 12 mm diameter hole drilled. | Nr | 42
8.4 | - Ditto - 100 mm diameter uPVC Class 'E' pipe 1700 mm long lateral with 8 pairs of 10 mm diameter holes | Nr | 84
8.5 | - Ditto - 100 mm diameter uPVC end cap | Nr | 84
8.6 | - Ditto - 100 mm diameter uPVC faucet socket with G.I. male threaded on one end and PVC socket on the other end | Nr | 84
8.7 | - Ditto - 12 mm diameter brass nipple with anticlockwise and clockwise (B.S.F.) threads | Nr | 42
Filter Media
8.8 | Provide gravel and form filters bed to the details shown on Drg. No. TWWDA/KTW/FFG-03 | m² | 44
8.9 | Provide sand and form filter sand bed to the details shown on Drg. No. TWWDA/KTW/FFG-03 | m² | 44
Support Brackets - Provide and Fix:
8.1 | Mass Concrete Class 20/20 finished fair on all surfaces support blocks 220 mm x 100 mm x 180 mm for brackets for uPVC laterals with half round groove for resting laterals as detailed on Drg. No. TWWDA/KTW/FFG-08. Include fixing with mortar. Include for top GMS support plate & bolts as detailed. | Nr | 126
PAGE TOTAL CARRIED TO SECTION COLLECTION SHEET
9 | METAL WORK
All steelwork to be completely cleaned by acid dipping prior to galvanising.
9.1 | Provide and fix 6 mm GMS deflector plate with 45o crank at 150 mm from one end fixed to concrete with 4 nr. 12 mm diameter rawl bolts as detailed on Drg. No. TWWDA/KTW/FFG-03. | Nr | 4
9.2 | Provide and fix C.I. Medium duty inspection cover size 600 mm x 450 mm with frames on filtered water channel | Nr | 1
9.3 | Provide and fix 900 mm high level balustrades of 40 mm diameter tubing Class 'B' throghout consisting of handrail and parallel middle rail 450mm below the handrail with balusters at maximum 1500 mm centres, all as detailed | m | 35
9.4 | Provide and fix balustrade unit 1000 mm high comprising 32 mm diameter galvanised pipe top,middle and bottom end bent, fanged and built into mortice in concrete. | m | 30
10 | MISCELLANEOUS
10.1 | Boxing out 1000 mm x 450 mm holes in Filter Gallery concrete wall for wash water Channel exit to wash water Chamber and making good after construction of the Channel. | Nr | 1
10.2 | - Ditto - but 600 mm x 550 mm holes on filter/overflow wash water reinforced concrete wall for wash water trough. | Nr | 4
10.3 | - Ditto - but 450 mm x 250 mm holes | Nr | 6
10.4 | - Ditto - but 250 mm x 250 mm holes in settled/filter inlet channel wall for inlet penstock | Nr | 4
10.5 | Boxing out 350 mm dia. holes in the side walls of the filter gallery for wash water inlet pipe and making good after pipe laid | Nr | 1
10.6 | - Ditto - but 300 mm dia. holes for filtered water pipes and backwash water pipes | Nr | 12
10.7 | - Ditto - but 200mm dia. holes in filtered water channel for filtered water outlet pipes | Nr | 4
10.8 | - Ditto - but 350mm dia. Holes in filtered water channel wall for filtered water outlet to the tank | Nr | 1
10.1 | Ditto -but for 100mm dia holes for Air Wash Pipe | Nr | 5
10.11 | - Ditto - but 600 mm x 450 mm holes for inspection chambers on the roof slab of filteres water channel | Nr | 2
10.12 | Allow for cutting, grouting and making good any holes, chases etc. for all fittings and pipework fixing and electrical work in the filters, filter gallery and filter control room | Item | L.S
10.13 | Provide all materials and fix to concrete air pipe supports as per details on Drg No. TWWDA/KTW/FFG-07 include for 3 coats of paint | Nr | 4
10.14 | Allow for leak proof testing of all the filters as specified | Item | L.S
10.15 | Provide, prepare and apply one coat mordant solution, one undercoat and two coats gloss enamel paint on galvanised metalwork externally on handrail pipe and fittings in 900 mm high level balustrade. | m | 70
10.16 | Ditto-but for a 1000mm high raking balustrade | m | 10
10.17 | Provide concrete support for washwater outlet and overflow measuring 775mm x 400mm x 300mm high with bituminous felt padding and 80mm x 6mm hick flat flat Gms plate anchored to the support by 2 nr. 6mm diameter bolts as per detail on Drg. No. TWWDA/KTW/FFG-05 | Nr | 2
10.18 | Provide mass concrete class 15/20 thrust blocks under 200mm dia. gate valves as per details on Drg. No. TWWDA/KTW/FFG-04 | Nr | 2
10.19 | -Ditto - but for 300mm dia. gate valve as per details on Drg. No. TWWDA/KTW/FFG-05 | Nr | 2
10.2 | -Ditto but under 200mm dia. gate valves as per details on Drg. No. TWWDA/KTW/FFG-04 | Nr | 2
10.21 | Allow for painting of all filtered water pipework to approved standards with 3 coats of super gloss paint applied on one coat primer. Colour selection to be approved by the Engineer. | Item | L.S
10.22 | Ditto- but for washwater inlet and washwater outlet pipework, Air wash pipework and overflow pipework. | Item | L.S
10.25 | Provide & fix over settled water channel precast concrete walkway slabs 950mm x 400mm x 75mm thick with 2No. mild steel key holes as per details on Drg. No. TWWDA/KTW/FFG-03 | Nr | 19
10.26 | Provide all materials (including tile adhesive, etc) and fix white ceramic tiles in filtered water channel as shown on Drg. No. TWWDA/KTW/FFG-08 | m² | 30
10.27 | Provide and apply Epoxy wall and floor coating, 'MASTERTOP 1110T' or approved equivalent, on internal surfaces of filter walls and floor. | m² | 201
PAGE TOTAL CARRIED TO SECTION COLLECTION SHEET
11 | PIPEWORK, FITTINGS & VALVES
Supply, transport to site and store in secure place, including jointing material, bolts, gaskets, packing, jointing glues, etc. as applicable
Note: Dimensions of Pipes and Fittings to be as shown on Drgs. Nos.TWWDA/KTW/FFG-10
Filter inlet
11.1 | 250 mm C.I. square Inlet Control penstock non-rising stem type complete with extension spindle and headstock with handwheel HamBaker or approved equivalent. | Nr | 2
Air Main Pipework - Approved lined ferrous pipes
11.2 | 100mm dia. flanged spigot pipe 4105mm long with spigot end blanked off and 21Nr. 12mm dia. holes and hexagon nuts welded at 215mm and 310mm c/c on underside as per details (Mark a) | Nr | 2
11.3 | 100mm dia. all flanged special tee with 2Nr. 12mm dia. holes and hexagon nuts welded at 215mm c/c on underside (Mark b) | Nr | 2
11.4 | 100mm dia. flanged spigot pipe 205mm long with spigot end blanked off and 1Nr. 12mm dia. hole and hexagon nut welded at 90mm from spigot end as per details (Mark c) | Nr | 2
11.5 | 100 mm dia. all flanged pipe, 2950 mm long (Mark d) | Nr | 2
11.6 | 100 mm dia. all flanged 90° bend (Mark e) | Nr | 6
11.7 | 100 mm dia. flanged spigot pipe, 1757 mm long (Mark f) | Nr | 2
11.8 | 100 mm dia. flange adaptor (Mark g) | Nr | 2
11.9 | 100 mm dia. all flanged gate valve with extended non-rising spindle length 410mm and headstock with handwheel to SRN 501 (Mark h) | Nr | 2
11.1 | 100mm x 100mm dia. all flanged tee (Mark i) | Nr | 2
11.11 | 100mm dia. all flanged pipe, 3160mm long (Mark j) | Nr | 2 |  |  |  | 0
11.12 | 100mm dia. blank flange (Mark k) | Nr | 2
11.13 | 100mm dia. all flanged pipe, 1774mm long (Mark l) | Nr | 2
11.14 | 100mm dia. flanged spigot pipe 4000mm long (cut to suit on site) (Mark m) | Nr | 2
11.15 | 100mm dia. flange adaptor (Mark n) | Nr | 2
11.16 | 100mm dia. flanged spigot pipe 1200mm long (Mark o) | Nr | 2
11.17 | 100mm dia. Flanged non-return valve (Mark p) | Nr | 2
11.18 | 150mm x 100mm double flanged concentric taper (Mark q) | Nr | 2
11.19 | 150mm dia. flanged spigot pipe 1200mm long (Mark r) | Nr | 2
Filtered Water Outlet Pipework - Approved Lined Ferrous Pipes
11.2 | 300mm dia. special flanged bellmouth 500mm long with puddle flange at 100mm from bellmouth end (Mark 1) | Nr | 2
11.19 | 300mm dia. all flanged pipe, 1520mm long with puddle flange at 500mm from one end (Mark 2) | Nr | 2
11.2 | Special all flanged cross 300mm x 300mm x 300mm x 300mm (Mark 3) | Nr | 2
11.21 | 300mm x 200mm dia. all flanged concentric taper (Mark 4) | Nr | 4
11.22 | 200mm dia. all flanged gate valve with extension spindle, length 4.8m and headstock with handwheel to SRN 501 (Mark 5) | Nr | 2
11.23 | 200mm dia. flanged spigot 90° bend (Mark 6) | Nr | 2
11.24 | 200mm dia. all flanged gate valve, with extension spindle, length 4.8m and headstock with handwheel to SRN 501 (Mark 7) | Nr | 2
11.25 | 200mm dia. flange adaptor (Mark 8) | Nr | 2
11.26 | 200mm dia. plain ended pipe 475mm long with puddle flange at 75mm from one end (Mark 9) | Nr | 2
Washwater Inlet - Approved Lined Ferrous Pipes
11.27 | 300mm dia. all flanged gate valve with extension spindle, length 4.8m and headstock with handwheel to SRN 501 (Mark 10) | Nr | 2
11.28 | 300mm dia. all flanged 900 short radius special bend (Mark 11) | Nr | 4
11.29 | 300mm dia. all flanged pipe 2000mm long (Mark 12) | Nr | 2
11.3 | 350mm x 350mm x 300mm dia. all flanged tee (Mark 13) | Nr | 2
11.31 | 350mm dia. blank flange (Mark 14) | Nr | 1
11.32 | 350mm dia. all flanged pipe 2850mm long (Mark 15) | Nr | 2
11.33 | 350mm dia. all flanged pipe 3950mm long (Mark 16) | Nr | 1
11.34 | 350mm dia. all flanged 90° short radius bend (Mark 17) | Nr | 1
11.35 | 350mm dia. flanged spigot pipe 2000mm long (Length cut to suit on site) (Mark 17A) | Nr | 1
11.36 | 350mm dia. flange adaptor (Mark 17B) | Nr | 1
11.37 | 350mm dia. flanged spigot pipe 1200mm long (Mark 17C) | Nr | 1
11.38 | 350mm dia. coupling (Mark 17D) | Nr | 1
Washwater Outlet - Approved Lined Ferrous Pipes
11.39 | 300mm dia. flanged spigot pipe 525mm long with puddle flange at 150mm from spigot end (Mark 18) | Nr | 2
11.4 | 300mm dia. all flanged 90° short radius special bend (Mark 19) | Nr | 2
11.41 | 300mm dia. all flanged gate valve with extended non-rising spindle, length 4.0m and non-rising type headstock with handwheel to SRN 501 (Mark 20) | Nr | 2
11.42 | 300mm dia. special flanged spigot 900 short radius bend (Mark 21) | Nr | 2
Overflow Pipework - Approved Lined Ferrous Pipes
11.43 | 200mm dia. flanged spigot pipe 470mm long with puddle flange at 150mm from spigot end (Mark 22) | Nr | 2
11.44 | 200mm dia. all flanged 90° bend (Mark 23) | Nr | 2
11.45 | 200mm dia. flanged spigot pipe, 3675mm long (Mark 24) | Nr | 2
Filtered Water Outlet to Treated Water Tank Pipework
11.46 | 350mm dia flanged spigot pipe 15000mm long with puddle flange at 100 mm from the spigot end;600mm long (mark 25) | Nr | 1
11.47 | 350mm dia coupling (Mark 26) | Nr | 1
Transport From Site Store, Install, Test & Commission
Filter inlet
11.48 | 250 mm C.I. square Inlet Control penstock non-rising stem type complete with extension spindle and headstock with handwheel HamBaker or approved equivalent. | Nr | 2
Air Main Pipework - Approved lined ferrous pipes
11.49 | 100mm dia. flanged spigot pipe 4105mm long with spigot end blanked off and 21Nr. 12mm dia. holes and hexagon nuts welded at 215mm and 310mm c/c on underside as per details (Mark a) | Nr | 2
11.5 | 100mm dia. all flanged special tee with 2Nr. 12mm dia. holes and hexagon nuts welded at 215mm c/c on underside (Mark b) | Nr | 2
11.51 | 100mm dia. flanged spigot pipe 205mm long with spigot end blanked off and 1Nr. 12mm dia. hole and hexagon nut welded at 90mm from spigot end as per details (Mark c) | Nr | 2
11.52 | 100 mm dia. all flanged pipe, 2950 mm long (Mark d) | Nr | 2
11.53 | 100 mm dia. all flanged 90° bend (Mark e) | Nr | 3
11.54 | 100 mm dia. flanged spigot pipe, 1757 mm long (Mark f) | Nr | 2
11.55 | 100 mm dia. flange adaptor (Mark g) | Nr | 2
11.56 | 100 mm dia. all flanged gate valve with extended non-rising spindle length 410mm and headstock with handwheel to SRN 501 (Mark h) | Nr | 2
11.57 | 100mm x 100mm dia. all flanged tee (Mark i) | Nr | 2
11.58 | 100mm dia. all flanged pipe, 3160mm long (Mark j) | Nr | 2
11.59 | 100mm dia. blank flange (Mark k) | Nr | 1
11.6 | 100mm dia. all flanged pipe, 2685mm long (Mark l) | Nr | 1
11.61 | 100mm dia. flanged spigot pipe 4000mm long (cut to suit on site) (Mark m) | Nr | 1
11.62 | 100mm dia. flange adaptor (Mark n) | Nr | 1
11.63 | 100mm dia. flanged spigot pipe 1200mm long (Mark o) | Nr | 1
11.64 | 100mm dia. Flanged non-return valve (Mark p) | Nr | 1
| 150mm x 100mm flanged concentirc taper (Mark q) | Nr | 1
| 150mm dia. flanged spigot pipe 1200mm long (Mark r) | Nr | 1
Filtered Water Outlet Pipework - Approved Lined Ferrous Pipes
11.65 | 300mm dia. special flanged bellmouth 500mm long with puddle flange at 100mm from bellmouth end (Mark 1) | Nr | 2
11.66 | 300mm dia. all flanged pipe, 1520mm long with puddle flange at 500mm from one end (Mark 2) | Nr | 2
11.67 | Special all flanged cross 300mm x 300mm x 300mm x 300mm (Mark 3) | Nr | 2
11.68 | 300mm x 200mm dia. all flanged concentric taper (Mark 4) | Nr | 4
11.69 | 200mm dia. all flanged gate valve with extension spindle, length 4.8m and headstock with handwheel to SRN 501 (Mark 5) | Nr | 2
11.7 | 200mm dia. flanged spigot 90° bend (Mark 6) | Nr | 2
11.71 | 200mm dia. all flanged butterfly valve, with extension spindle, length 4.8m and headstock with handwheel to SRN 501 (Mark 7) | Nr | 2
11.72 | 200mm dia. flange adaptor (Mark 8) | Nr | 2
11.73 | 200mm dia. plain ended pipe 475mm long with puddle flange at 75mm from one end (Mark 9) | Nr | 2
Washwater Inlet - Approved Lined Ferrous Pipes
11.74 | 300mm dia. all flanged gate valve with extension spindle, length 4.8m and Headstock with handwheel to SRN 501 (Mark 10) | Nr | 2
11.75 | 300mm dia. all flanged 90° short radius special bend (Mark 11) | Nr | 4
11.76 | 300mm dia. all flanged pipe 2000mm long (Mark 12) | Nr | 2
11.77 | 350mm x 350mm x 300mm dia. all flanged tee (Mark 13) | Nr | 2
11.78 | 350mm dia. Blank flange (Mark 14) | Nr | 1
11.79 | 350mm dia. all flanged pipe 2850mm long (Mark 15) | Nr | 2
11.8 | 350mm dia. all flanged pipe 3950mm long (Mark 16) | Nr | 1
11.81 | 350mm dia. all flanged 90° short radius bend (Mark 17) | Nr | 1
11.82 | 350mm dia. flanged spigot pipe 2000mm long (Length cut to suit on site) (Mark 17A) | Nr | 1
11.83 | 350mm dia. flange adaptor (Mark 17B) | Nr | 1
11.84 | 350mm dia. flanged spigot pipe 1200mm long (Mark 17C) | Nr | 1
11.85 | 350mm dia. coupling (Mark 17D) | Nr | 1
Washwater Outlet - Approved Lined Ferrous Pipes
11.86 | 300 mm dia. flanged spigot pipe, 525 mm long with puddle flange at 150mm from spigot end (Mark 18) | Nr | 2
11.87 | 300 mm dia. all flanged 90o short radius special bend (Mark 19) | Nr | 2
11.88 | 300mm dia.all flanged gate valve with extended non-rising spindle, length 4.0m and non-rising type headstock with hand wheel to SRN 501(Mark 20) | Nr | 2
11.89 | 300 mm dia. special flanged spigot 90° short radius bend (Mark 21) | Nr | 2
Overflow Pipework - Approved Lined Ferrous Pipes
11.9 | 200mm dia. flanged spigot pipe 470mm long with puddle flange at 150mm from spigot end (Mark 22) | Nr | 2
11.91 | 200mm dia. all flanged 900 bend (Mark 23) | Nr | 2
11.92 | 200mm dia. flanged spigot pipe, 3675mm long (Mark 24) | Nr | 2
Filtered Water Outlet to Treated Water Tank Pipework
11.93 | 350mm dia flanged spigot pipe 470mm long with puddle flange at 150 mm from the spigot end;600mm long (mark 25) | Nr | 1
11.94 | 350mm dia coupling (Mark 26) | Nr | 1
PAGE TOTAL CARRIED TO SECTION COLLECTION SHEET
COLLECTION SHEET
FILTERS AND FILTER GALLERY
Collection 1
Collection 2
Collection 3
Collection 4
Collection 5
Collection 6
Collection 7
TOTAL INCLUSIVE OF V.A.T FOR FILTERS AND FILTER GALLERY CARRIED TO SUMMARY PAGE

## WaterTank
BILL No. 5
KAHARO - TREATED WATER TANK (150m³ CAPACITY)
ITEM | DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
No. |  |  |  | (Kshs) | (Kshs)
CLASS D - SITE CLEARANCE
D11 | General clearance of all shrubs. | ha | 0.03
CLASS E - EARTHWORKS.
General Excavation for Foundations
Excavation for structures: material other than top soil, rock or artificial hard material for attaining the proposed sub grade, haul up to stockpiles on designated area to be determined by the Department.
E411 | Excavation for structures; depth not exceeding 0.25m. | m3 | 19.7
E422 | General Excavation ;depth 0.25 - 0.5m. | m3 | 19.7
E423 | General Excavation ;depth 0.5 - 1m. | m3 | 39.25
E424 | General Excavation ;depth 1 - 2m. | m3 | 78.5
E425 | General Excavation ;depth exceeding 2m | m3 | 78.5
Filling
E614 | Filling to structure using suitable excavated materials | m3 | 11.78
E615 | Filling to structure using suitable imported materials from borrow pit. -Hardcore fill. | m3 | 23.55
E645 | 50 mm Blinding layer using quary dust. | m3 | 4
Filling Ancillaries
E722 | Preparation of filled surfaces to receive permanent work. | m2 | 78.5
CLASS F - INSITU CONCRETE
Provision of concrete - designed concrete
F233 | Concrete Class C15/20 to 100mm thick blinding layer. | m3 | 3.7
F253 | Concrete Class C25/20 to ground slab | m3 | 26
F253 | Concrete Class C25/20 to cover slab | m3 | 10.4
F253 | Concrete Class C25/20 to central column | m3 | 0.3
PAGE TOTAL CARRIED TO SECTION COLLECTION SHEET
CONCRETE ANCILLARIES
Placing of concrete
F651 | Blinding concrete not exceeding 150mm thick. | m3 | 3.7
F622 | Reinforced concrete to ground slab | m3 | 26
F632 | Reinforced concrete to cover slab. | m3 | 10.4
F632.3 | Reinforced concrete to central column | m3 | 0.3
FORWORK
G245.1 | Fair finish sides of ground slab - 200 mm deep. | m2 | 25.4
G245.2 | Fair finish sides of cover slab - 200 mm deep. | m2 | 10.9
G215 | Fair finish soffit of cover slab. | m2 | 72.5
G243 | Fair finish to central column | m2 | 3.5
REINFORCEMENT
G523 | Nominal diameter 8mm | kg | 346
G524.1 | Nominal diameter 12mm | kg | 3080
G525.2 | Nominal diameter 16mm | kg | 2108
Concrete Accessories
G812.1 | Steel trowel Finishing to top surface of base slab | m2 | 72.3
G812.2 | Steel trowel finish to sofit and top of cover slab. | m2 | 72.3
BRICKWORK, BLOCKWORK AND MASONRY
Concrete masonry units bedded in mortar flush pointed including reinforcement using Y8 reinforcement bars for every alternate course.
U521 | 150 - 250mm mm thick solid blockwork | m2 | 58.5
U531 | 250 - 500mm mm thick solid blockwork | m2 | 35.1
JOINT
V754 | Provide and apply 20x20mm bondex filler at the tank bottom joint | m | 29.3
V857 | Provide and apply Bituminous paint on the slab -stone joints at the floor and roof slabs. | m2 | 17.6
CLASS Z: FINISHES
Z413.1 | 30mm thick two coat sulphate resisting plaster to all internal surfaces including water proofing additives | m2 | 86
Z413.2 | 20mm thick one coat sulphate resisting plaster to all external surfaces including water proofing additives | m2 | 93.5
Z413.3 | 50mm thick screed three coat sulphate resisting screed to floor surfaces including water proofing additives | m2 | 57.4
PAGE TOTAL CARRIED TO SECTION COLLECTION SHEET |  |  |  |  | 0
CHAMBERS
K | CLASS K: PIPE WORK - CHAMBERS AND PIPE WORK ANCILLARIES
Chambers, ducts, culverts, crossings, thrust and anchor blocks, reinstatement and others as listed and specified in drawings.
Note:- Items for work in this class shall include:- - Excavation, preparation of surfaces, disposal of excavated material, shoring sides of excavation, backfilling and removal of redundant services. - Concrete, reinforcement, formwork, joints and finishes. - Tips for disposal of excavated material or debris to be identified by the Contractor in liaison with the Local Authority.
K1 | Excavate for, provide all materials and construct complete chambers with lockable covers. Internal dimensions 1000mm x 1000 mm. Base slab to be 125 mm thick reinforced concrete and including cover slab of reinforced concrete. Rate to include for all thrust blocks, pipe supports, inspection covers etc as detailed in the drawings. Provide and place mass concrete grade 15 at outfalls to washouts including for all shuttering required as directed by the Resident Engineer.
K111.3 | Inlet,outlet and washout chambers | nr | 3
CLASS J: PIPEWORK - FITTINGS AND VALVES
Provide, handle, install and test the following steel and uPVC pipes and fittings, valves and specials. Rates shall include for completing all pipe joints as specified.
Inlet Steel Pipes and Steel Fittings
J352.1 | 250mm HDPE /GI Adaptor | nr | 1
J381.1 | 250mm x 1000mm long single flanged Pipe | nr | 2
J811 | 250mm Flanged Gate Valve | nr | 1
J352.2 | 250mm Flanged Adaptor | nr | 4
J352.3 | 350mm Flanged Adaptor | nr | 4
J311.1 | 250mm x 900 Double Flanged Bend | nr | 2
J832 | 250mm Double flanged beat equilibrium float valve | nr | 1
J371 | 1000mm Flanged Bell mouth | nr | 1
J371.1 | 350mm Flanged Bell mouth | nr | 1
J311.2 | 350mm x 900 Double Flanged Bend short radius bend | nr | 1
J311.3 | 100mm x 900 Double Flanged Bend short radius bend | nr | 1
J381.2 | 350mm x 2100mm long Single flanged pipe with puddle flange 500mm away from the flanged end. | nr | 1
J323 | 350mm x 225mm all flanged TEE | nr | 1
J352.4 | 350mm Blind Flange | nr | 1
J352.5 | 250mm Blind Flange | nr | 1
J332 | 250mm x 225mm Double Flanged Concentric taper | nr | 1
J352.6 | 250mm Flanged Gate Valve | nr | 1
J381.3 | 100mm x 1000mm long single flanged steel spigot pipe. | nr | 1
Overflow and Scour Steel Pipe and Fittings
J381.4 | 150mm x 600mm long Single Flanged pipe with central puddle | nr | 2
J311.4 | 150mm x 900 Double Flanged short radius bend | nr | 1
J351.1 | 150mm Flange Adaptor | nr | 1
J381.5 | 150mm x 2500mm long Single flanged pipe. | nr | 1
J311.5 | 150mm x 450 Double Flanged short radius bend | nr | 1
J381.6 | 150mm x 1500mm long Single flanged pipe with bevelled end | nr | 1
J381.7 | 150mm x 2100mm long Single flanged pipe with puddle flange 450mm from plain end. | nr | 1
J811.1 | 150mm Double Flanged Gate Valve | nr | 1
J811.2 | 225mm Double Flanged Gate Valve | nr | 1
J351.2 | 150mm HDPE/ GI adaptor | nr | 1
J381.8 | 225mm x 1000mm long single flanged Pipe | nr | 1
J381.9 | 100mm x 1000mm long single flanged Pipe | nr | 1
J352.7 | 225mm HDPE/ GI adaptor | nr | 1
I512 | 150mm Class C Upvc pipe | m | 6
Vent Pipe
J361 | Provide and fix 100mm vent pipes with gooze wire at the end. | nr | 2
PAGE TOTAL CARRIED TO SECTION COLLECTION SHEET
CLASS N: MISLENEOUS METAL WORK
Rate to include supply and fixing and inclusive of foundations where applicable.
N13.1 | Galvanised mild steel internal ladders with stringers returned to form handrails.Length as shown in the drawings. | nr | 1
N13.1 | Galvanised mild steel external ladders with stringers returned to form handrail.Length as shown in the drawings. | nr | 1
CLASS X:MISCELLANEOUS WORK
X136 | Provide all materials and construct concrete post and Chainlink fence as shown in the drawings. Height : 2.50 - 3.00 m | m | 76
X234 | Provide and install metal gate, width:3 m. | nr | 1
PAGE TOTAL CARRIED TO SECTION COLLECTION SHEET
COLLECTION PAGE
500M3 CLEAR WATER TANK
Collection 1
Collection 2
Collection 3
Collection 4
TOTAL INCLUSIVE OF V.A.T FOR 150M3 CLEAR WATER TANK CARRIED TO SUMMARY PAGE

## Pumphouse
BILL No. 6
KAHARO - PUMP HOUSE
ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
No. |  |  |  | (Kshs) | (Kshs) | cts
SUB-STRUCTURE
1 | EXCAVATION
The rates shall include for all strutting, shuttering, stabilising the excavation faces, and keeping the excavation free of water by pumping, bailing or other means.
Bulk excavations and top soil stripping for all structures are measured under General Site Clearance.
Excavate below stripped level to formation level in common material, part backfill after construction and remainder, cart away to tips or use as fill on site, all as directed by the Engineer.
1.1 | Maximum depth n.e. 1.0 m | m3 | 110
1.2 | -Ditto- but maximum depth 1.0 m to 2.0 m | m3 | 60
1.3 | -Ditto- but maximum depth 2.0 m to 3.0 m | m3 | 2
Extra Over Excavation in Any Position for:-
1.4 | Excavating in rock Class "A" | m3 | 11
1.5 | Excavating in rock Class "B" | m3 | 1
1.6 | Excavating in rock Class "C" | m3 | 1
Approved Selected Filling as Described:-
1.7 | Provide and deposit approved selected fill in maximum 150mm thick layers in making up levels including achieving satisfactory compaction. Rate to include performing necessary compaction tests. | m3 | 20
1.8 | Provide, lay and level out fine crushed stone, sand or gravel blinding 50mm thick to surface of filling, including watering and rolling to achieve satisfactory compaction. | m2 | 54
1.9 | Fill with approved hardcore in a 300mm thick layer including achieving satisfactory compaction. | m2 | 54
Disposal of Surplus Spoil:-
1.1 | Cart away surplus excavated materials to an approved dumping site | m3 | 20
Anti-Termite Treatment
1.11 | Chemical anti-termite treatment to surface of filling with an approved insecticide. | m2 | 15
Damp-Proof Membrane
1.12 | 500 Gauge polythene sheeting, laid over hardcore in two layers | m2 | 15
CONCRETE WORK
Mass Concrete Class 15/20mm Maximum Aggregate as Described in:-
1.13 | 75mm Thick blinding under the walls strip footings, column bases and over hardcore | m2 | 10 |  |  |  | 6.8
Guaranteed Strength Reinforced Concrete Class 25/20mm Maximum Aggregate as Described in:-
1.14 | 300mm Thick Base Slab | m3 | 5
1.15 | 150mm Thick Base Slab | m3 | 5
1.16 | 300mm Thick Column Bases and Wall Strip Footings | m3 | 2
1.17 | Isolated columns and piers in foundations | m3 | 1
1.18 | Pump Plinth size 1500mm long x 650mm wide x 300mm deep | Nr | 2
Builders Work
1.19 | Drainage sump internal size 400mm long x400mm wide x 1000mm deep made out of 150mm thick reinforced concrete base and walls including forming rebate 50mm wide x 75mm deep to top inner edges of sump wall to receive chequer plate cover (m.s.) and including all necessary excavation, disposal and formwork. | Nr | 1
1.2 | Form cable duct internal size 200mm wide x 150mm deep in concrete floor slab including forming rebate 50mm wide x 75mm deep to top inner edges of channel wall to receive chequer plate cover (m.s.) | m | 14
1.21 | Form drainage channel internal size 150mm wide and depth varying from 150mm to 200mm deep in concrete floor slab including forming rebate 50mm wide x 75mm deep to top inner edges of channel wall to receive mild steel grating cover (m.s.) | m | 6
1.22 | Provide all materials and install a 100mm Dia. Upvc drainage pipe cast into floor slab | m | 3
1.243 | Form pocket internal size 1500mm long x 650mm wide x 300mm deep in base slab to receive pump plinth (R.C.) including all the necessary formwork | Nr | 2
Guaranteed Strength Reinforced Concrete Class 25/20mm Maximum Aggregate as Described in:-
1.24 | 100mm Thick ramp laid to slope not exceeding 15 degrees from horizontal | m3 | 1
1.25 | Extra over for tamping concrete whilst still green to make ribbed finish of the ramp area. | m2 | 5
Fabric Reinforcement No. A142 Mesh Size 150 x 150mm Weighing 2.22 kgs Per m2 , Including Bends, Tying Wire and Distance Blocks:-
1.26 | Fabric reinforcement with minimum 150mm wide side and end laps, laid in bed | m2 | 5
Provide and Fix High Tensile Steel Reinforcement to SRN 127 including Cutting, Bending, Propping With Spacers and Tying as Specified :-
1.27 | Reinforcement, all diameters | Kg | 3300
FORMWORK
Provide and Fix Shuttering Including Propping, Strutting and Striking, all as Specified
Sawn Formwork - Class F1 Finish:-
1.28 | Sides of 300mm thick pump house base slab | m2 | 11
1.29 | Sides of 150mm thick pump house base slab | m2 | 1
1.3 | Sides of 300mm column bases and columns in the foundations | m2 | 10
1.31 | Sides of 300mm Walls Strip footings - Pump house walls | m2 | 20
1.32 | Drainage sump internal size 400mm long x400mm wide x 1000mm deep made out of 150mm thick reinforced concrete base and walls including forming rebate 50mm wide x 75mm deep to top inner edges of sump wall to receive chequer plate cover (m.s.) and including all necessary excavation, disposal and formwork | m2 | 1
1.33 | Form cable duct internal size 200mm wide x 250mm deep in concrete floor slab including forming rebate 50mm wide x 75mm deep to top inner edges of channel wall to receive mild steel grating cover (m.s.) | m2 | 7
1.34 | Form drainage channel internal size 150mm wide and depth varying from 150mm to 200mm deep in concrete floor slab including forming rebate 50mm wide x 75mm deep to top inner edges of channel wall to receive mild steel grating cover (m.s.) | m2 | 3
Wrot Formwork - Class F3 Finish:-
1.35 | Edges of Pump Plinth size 1600mm long x 650mm wide x 300mm deep not exceeding 300mm wide | m | 11
RENDERING
15mm Cement and sand (1:4) render to plinths, finished with a wood float
1.36 | Pump Plinth size 1600mm long x 650mm wide x 300mm deep including pocket in base slab | m2 | 5
Bonded Cement and Sand (1:4) Screed Bed in One Coat with Approved Hardener incorporated in the Mix, Well Bonded to Concrete Base as Described:-
1.37 | 40mm Thick paving with wood float finish on pump house slab | m2 | 20
PAINTING AND DECORATING
1.38 | Prepare and apply two coats of bituminous paint on rendered plinth walls | m2 | 19
1.39 | Provide and apply approved industrial Epoxy floor paint on the Pump House Floor. | m2 | 20
Damp-proof course:
Bituminous Felt Damp-Proof Course as Described:-
1.4 | 200mm Wide under walls | m | 15
Joint Filler
1.41 | 20mm Thick resin bonded cork filler between 1600 x 650 x 300mm pump plinth and 300mm thick floor slab sealed with 25mm deep bitumen | m2 | 5
Walling
Natural Stone Block Walling, Medium Chisel Dressed, Reinforced with 20 swg Hoop Iron at every third course, and Bedded, Jointed and Pointed in Cement Mortar (1:4):-
1.42 | 200 mm Walling | m2 | 15
SUPERSTRUCTURE
CONCRETE WORKS
Guaranteed Strength Reinforced Concrete Class 25/20mm as Described in:
1.43 | Upstand for the control panel | m3 | 1
1.44 | Columns | m3 | 2
1.45 | Beams | m3 | 3
Precast Concrete Paving Slabs
1.46 | Slabs size 600 x 600 x 50mm Thick laid on and including 50mm thick bed of sand and jointing and pointing in cement mortar | m2 | 50
REINFORCEMENT
Provide and Fix High Tensile Steel Reinforcement to SRN 127 including Cutting, Bending, Propping with Spacers and Tying as Specified :-
1.47 | Reinforcement, all diameters | kg | 720
FORMWORK
Provide and Fix Shuttering Including Propping, Strutting and Striking, all as Specified.
1.48 | Upstand for the control panel, columns and beams in the superstructure. | m2 | 35
WALLING
Selected Machine Dressed Natural Stone Block Walling, Reinforced with 20 swg Hoop Iron at Every Third Courses, and Bedded, Jointed and Pointed in Cement Mortar (1:5):-
1.49 | 200mm Thick walling | m2 | 30
Labours
1.5 | Extra over walling for ruled horizontal and flush vertical joints | m2 | 12
Precast Concrete Cills
1.51 | 200mm Thick x 275mm wide precast concrete cill bedded, jointed and pointed in cement mortar on top of 200mm wall | m | 8
PLASTERING
1.52 | 12.5mm thick cement gauged plaster internally on blockwork surfaces | m2 | 30
RENDERING
1.53 | 12.5mm thick cement and sand rendering externally on concrete surfaces | m2 | 10
METALWORK
Rates to include for Provision of all Material, Fabrication and Fixing
Floor Gratings
1.54 | Mild steel grating drain channel cover 140mm wide x 2900mm long made out of 16mm round m.s transverse bars welded at 20mm spacing to 16mm round m.s longitudinal bars welded to 38 x 38 x 6mm thick m.s angles | m2 | 2
1.56 | Mild steel chequer plate cover for cable duct internal size 200mm wide x 150mm deep | m2 | 3
Steel Doors
Pressed Metal Louvre Doors
Supply and Fix the Following Pressed Metal Louvre Doors with 100 x 50mm Stiles and Top Rails, 150 x 50mm Middle and Bottom Rails With Pressed Metal Infill Louvres and 100 x 50mm Pressed Metal Frames, Including Hinges, Pad Bolts and Tower Bolts, All To Manufacturer's Details, With Three Coats Gloss Paint Complete With Opening Accessories Including Bedding and Pointing Around Frames in Cement Mortar:-
1.57 | Double door size 1200 x 2400 mm high in two equal panels | Nr | 1
Steel Casement Windows
Supply and Fix the following Standard Section Steel Casement Windows, including 4mm Thick Clear Sheet Glass glazed to Steel Casements with putty, complete with the following, all finished with three coats oil paint:-
- Opening accessories, including building in lugs to jambs and head and water-proofing and filling around opening with approved compound
- Solid Timber Window Board, 200mm wide x 25mm thick, exposed edge with bull-nose finish
- Burglar-Proofing Fabricated from 12 x 12mm Mild Steel Square Bars at 150mm Centres Vertically and 150mm Horizontally and Fixed Internally to Surrounding Wall with 12mm Mild Steel Fish-Tailed Lugs at Maximum 600mm Centres;
1.58 | Window size 1200 x 1200mm high in 3 equal panels with upper part having 2 No. fixed and 1 No. top hung ventilator,and lower half having 2 No. side-hung panels opening outward and 1 No. fixed panel (W1) | Nr | 1
PVC Gauze Screen set on and including a Timber Framing all Round and Fixing to Wall :-
1.59 | Gauze size 1275 x 600mm high | Nr | 4
1.6 | Gauze size 1800 x 870mm high | Nr | 2
Precast Concrete Louvre Block Walling :-
1.66.1 | 200mm Thick louvre block walling with twin section with plastic coated coffee tray wire sandwiched between sections | m2 | 8
PAINTING AND DECORATING
Prepare and Apply Three Coats Exterior Quality Plastic Emulsion Paint:-
Externally on:-
1.62 | Fair-faced concrete surfaces | m2 | 10
Prepare and Apply Three Coats Interior Quality Plastic Emulsion Paint:-
Internally on:-
1.63 | Plastered blockwork and concrete surfaces | m2 | 30
1.64 | Allow for painting of all pipework within the Pump House with 3 coats of approved super gloss paint applied on 1 coat primer | Item | L.S
Prepare and Apply Three Coats Washable Distemper as Described to:-
1.65 | Horizontal soffites of suspended chipboard or plasterboard ceilings | m2 | 15
ROOF COVERINGS
Concrete, Single Lap Interlocking Roof Tiles on and Including Sawn Cypress (Grade 2) Battens Size 40 x 40mm Pressure Impregnated with Approved Preservative:-
1.66 | Roof tiles | m2 | 15 |  |  | 1
Extra Over Roofing Tiles for:-
1.67 | Ridge capping including bedding and pointing in cement sand (1:4) mortar with colouring to match colour of tiles | m | 3
1.68 | Hip capping ditto | m | 18
1.69 | Filled ends of ridge capping or hip capping | Nr | 6
1.7 | Fair raking cutting roofing tiles | m | 18
1.71 | Gauge 28 galvanised plain sheets as laid as underlay and nailed to rafters (m²) | m2 | 15
CARPENTRY AND JOINERY
Carpentry
Roof Trusses
Double Pitch Roof Truss With 600mm Eaves Projection, in 150 x 50mm Rafters, Ceiling joists, Struts and Ties in Sawn Cypress Grade II Seasoned and Pressure Impregnated with Wood Preservative and timber joints with Bolted and Nailed Connections to the Engineer's Approval :-
1.72 | Equal truss 3600mm clear span and 1560mm high at 1500mm c/c | Nr | 2
Other Roof Members
Sawn Cypress Grade II Maximum Moisture Content 12% Seasoned and Pressure Impregnated with Wood Preservative and Timber Joints With Bolted and Nailed Connections to the Engineer's Approval:-
1.73 | 150 x 50mm Intermediate and hip rafters | m | 45
1.74 | 150 x 75mm Purlins | m | 9
1.75 | 180 x 50mm Ridge board | m | 3
1.76 | 100 x 50mm Wall plate tied to wall with 20 s.w.g. hoop iron at 900mm centres and bedded in cement mortar (1:4) on top of wall | m | 15
Joinery
General Timbers
Wrot Prime Grade Cypress, Including Finishing With Three Coats First Quality Gloss Paint :-
1.77 | 250 x 40mm Fascia board, fixed with screws | m | 15 |  |  | 1
PAGE TOTAL CARRIED TO SECTION COLLECTION SHEET
2 | CEILING
12mm Thick Approved Chipboard to BS 2604, Part 2, density 480-640kgs, per Square Meter in Sheets Size 2400 x 1200mm Fixed to and Including 50 x 50mm Sawn Cypress Grade 2 Battens at 600mm Centres in Both Directions Complete with Gauge Jointing Material
2.1 | Horizontal ceiling fixed to underside of trusses | m2 | 15 |  |  | 1
2.2 | 12mm Cornice 50mm high, plugged | m | 15 |  |  | 1
2.3 | Extra over ceiling lining for forming removable access trap door size 600 x 600mm with 100 x 38 mm sawn treated cypress trimming joists between tie beams,120 x 20mm (finished ) wrot cypress frame all round and 20mm blockboard removable panel set loose on top of framing. | Nr | 1
Builders Work in Connection with Electrical Installations
2.4 | Allow for cutting and leaving all necessary holes, notches, mortices, sinkings and chases both in the structure and its finishes and for all making good in connection with concealed conduits or cables | Item | L.S
PIPEWORK AND FITTINGS
Supply, Transport to Site and Store in Secure Place, Including Jointing Material, Bolts, Gaskets, Packing, Jointing Glues, etc. as Applicable
Backwash Pumps - Suction Main (Approved Lined Ferrous Pipe Fittings to Class NP 16)
2.5 | 200mm dia. special 90° bend, one end flanged, other end bellmouth shaped (Mark A) | Nr | 1
2.6 | 200mm dia. all flanged spigot pipe, length 1800mm with puddle flange 1000m from flanged end (Mark B) | Nr | 1
2.7 | 200mm dia. Flanged adapter (Mark C) | Nr | 1
2.8 | 200 mm dia. all Flanged 90° bend (Mark D) | Nr | 1
2.9 | 200mm dia. All Flanged, 1205mm long pipe (Mark E) | Nr | 1
2.1 | 200mm x 200mm dia. all flanged tee (Mark F) | Nr | 1
2.11 | 200mm × 150mm dia. all flanged tee (Mark G) | Nr | 1
2.12 | 200mm dia. Blank flange (Mark H) | Nr | 2
2.13 | 150mm dia. all flanged pipe 1075mm long with puddle flange at 450mm from one end (Mark I) | Nr | 1
2.14 | 150mm dia. Flange adaptor (Mark J) | Nr | 1
2.15 | 150mm double flange gate valve (Mark K) | Nr | 1
2.16 | 150mm x 80mm dia. Special all flanged eccentric taper (Mark L) | Nr | 1
Backwash Pumps - Delivery Main (Approved Lined Ferrous Pipe Fittings to Class NP 16)
2.17 | Special 100mm x 65mm all flanged concentric taper with 25mm dia. Male threaded tapping for pressure gauge (Mark 1) | Nr | 1
2.18 | 25mm dia. pressure gauge (pressure class up to 10 bars) - Hunter or approved equivalent (Mark 2) | Nr | 1
2.19 | 100mm dia. all flanged 90° bend (Mark 3) | Nr | 1
2.2 | 100mm dia. all flanged free acting check valve (Non return valve) (Mark 4) | Nr | 1
2.21 | 100mm dia. all flanged gate valve to BS 5163 (short face to face) (Mark 5) | Nr | 1
2.22 | 100mm dia. flange adaptor (Mark 6) | Nr | 2
2.23 | 100mm dia. flanged spigot pipe, length 1020mm (Mark 7) | Nr | 1
2.24 | 100mm × 100mm x 50mm dia. all flanged tee (Mark 8) | Nr | 1
2.25 | 50mm dia. Single orifice air valve with built in isolating valve (Mark 9) | Nr | 1
2.26 | 100mm dia. flanged spigot pipe 1405mm long (Mark 10) | Nr | 1
2.27 | 150mm x 100mm dia. all flanged tee (Mark 11) | Nr | 1
2.28 | 150mm dia. blank flange (Mark 12) | Nr | 1
2.29 | 150mm dia. all flanged pipe, length 900mm (Mark 13) | Nr | 1
2.3 | 150 mm dia. flanged 90° bend (Mark 14) | Nr | 1
| 150mm dia. Flanged spigot pipe, 1200mm long (Mark 15) | Nr | 1
2.31 | 150mm dia.Coupling (Mark 16) | Nr | 1
Transport From Site Store, Install, Test and Commission
Backwash Pumps - Suction Main (Approved Lined Ferrous Pipe Fittings to Class NP 16)
2.32 | 200mm dia. special 90° bend, one end flanged, other end bellmouth shaped (Mark A) | Nr | 1
2.33 | 200mm dia. all flanged spigot pipe, length 1800mm with puddle flange 1000m from flanged end (Mark B) | Nr | 1
2.34 | 200mm dia. Flanged adapter (Mark C) | Nr | 1
2.35 | 200 mm dia. all Flanged 90° bend (Mark D) | Nr | 1
2.36 | 200mm dia. All Flanged, 1205mm long pipe (Mark E) | Nr | 1
2.37 | 200mm x 200mm dia. all flanged tee (Mark F) | Nr | 1
2.38 | 200mm × 150mm dia. all flanged tee (Mark G) | Nr | 1
2.39 | 200mm dia. Blank flange (Mark H) | Nr | 2
2.4 | 150mm dia. all flanged pipe 1075mm long with puddle flange at 450mm from one end (Mark I) | Nr | 1
2.41 | 150mm dia. Flange adaptor (Mark J) | Nr | 1
2.42 | 150mm double flange gate valve (Mark K) | Nr | 1
2.43 | 150mm x 80mm dia. Special all flanged eccentric taper (Mark L) | Nr | 1
Backwash Pumps - Delivery Main (Approved Lined Ferrous Pipe Fittings to Class NP 16)
2.44 | Special 100mm x 65mm all flanged concentric taper with 25mm dia. Male threaded tapping for pressure gauge (Mark 1) | Nr | 1
2.45 | 25mm dia. pressure gauge (pressure class up to 10 bars) - Hunter or approved equivalent (Mark 2) | Nr | 1
2.46 | 100mm dia. all flanged 90° bend (Mark 3) | Nr | 1
2.47 | 100mm dia. all flanged free acting check valve (Non return valve) (Mark 4) | Nr | 1
2.48 | 100mm dia. all flanged gate valve to BS 5163 (short face to face) (Mark 5) | Nr | 1
2.49 | 100mm dia. flange adaptor (Mark 6) | Nr | 1
2.5 | 100mm dia. flanged spigot pipe, length 1020mm (Mark 7) | Nr | 1
2.51 | 100mm × 100mm x 50mm dia. all flanged tee (Mark 8) | Nr | 1
2.52 | 50mm dia. Single orifice air valve with built in isolating valve (Mark 9) | Nr | 1
2.53 | 100mm dia. flanged spigot pipe 1405mm long (Mark 10) | Nr | 1
2.54 | 150mm x 100mm dia. all flanged tee (Mark 11) | Nr | 1
2.55 | 150mm dia. blank flange (Mark 12) | Nr | 1
2.56 | 150mm dia. all flanged pipe, length 900mm (Mark 13) | Nr | 1
2.57 | 150 mm dia. flanged 90° bend (Mark 14) | Nr | 1
2.58 | 150mm dia. Flanged spigot pipe, 1200mm long (Mark 15) | Nr | 1
2.59 | 150mm dia.Coupling (Mark 16) | Nr | 1
PAGE TOTAL CARRIED TO SECTION COLLECTION SHEET
3 | PUMPS
Backwash Pumps
3.1 | Supply, transport to site, install, test and commission centrifugal pumps (1 duty) complete with motor, base plate, fixing bolts, grouting, etc., for the following characteristics: Flow 50m3 per hour, dynamic head 20m, KSB Etarnorm 80-250 or approved equivalent. | Nr | 1
4 | PIPE SUPPORTS AT BACKWASH PUMPS DELIVERY MAIN
4.1 | Supply and Install pipe support made of 100mm dia. pipe 1500mm long, welded to 6mm M.S plate at bottom, fixed to floor with 4Nrs. 16mm dia. Bolts | Item | L.S
PAGE TOTAL CARRIED TO COLLECTION SHEET
COLLECTION PAGE
PUMP HOUSE
Collection No. 1
Collection No. 2
Collection No. 3
TOTAL INCLUSIVE OF V.A.T FOR PUMP HOUSE CARRIED TO SUMMARY PAGE

## Pipeline
BILL NO. 7 - TREATED MAINLINE
ITEM | DESCRIPTION | Unit | QTY | RATE (KShs.) Inclusive of VAT | AMOUNT (KShs.)
1 | Clearance
1.1 | Clear line of all bushes and shrubs and remove debris from site average width 1.2m as directed by the Engineer | m | 4000
2 | EXCAVATION AND EARTHWORKS
2.1 | Excavate in pipe trench for pipe diameter 225mm, average of 1.2m but not exceeding 1.5m deep, minimum pipe cover 1000mm, backfilling after pipe fixing and disposal of excess material after backfilling | M | 3960
2.2 | Ditto excavation exceeding 1.5 m but not exceeding 3.0m | M | 440
2.5 | Extra over for excavation in rock as described and defined in the specifications.(Provisional) | M³ | 50
2.6 | Allow for compacted bedding and pipe surrounding (150mm thick all round the pipe) with approved selected excavated material in approved rocky areas to the satisfaction of the Engineer.(Provisional) | M | 100
2.7 | Allow for compacted pipe bedding and pipe surrounding (150mm thick all round the pipe) with approved imported material in approved rocky areas to the satisfaction of the Engineer.(Provisional) | M | 100
3 | Tree Cutting
Allow for cutting and disposal of trees, including cutting and disposal of of trunks, branches and removal and disposal of stumps, roots, and earth filling in the depression/pit.
3.1 | Girth from 300 mm to 600 | Nr. | 2
3.2 | Girth from 600 mm to 900 mm | Nr. | 1
3.3 | Girth from 900 mm to 1800 mm | Nr. | 1
4 | Pipework-Supply and Install
Supply, Lay and fuse HDPE pipes and fittings as described, rates to include necessary trimming alignment. Rates to include for Supply of pipes and associated appurtenances, transport to site, excavate for, lay, joint, test and backfill. The pipes and fittings are to be laid in accordance with Drawings provided and to the ngineers instructions
4.1 | OD 225mm HDPE PN10 | m | 3020
4.2 | OD 225mm HDPE PN12.5 | m | 590
4.3 | OD 225mm HDPE PN16 | m | 420
5 | Extra over for pipework in the following :-
Norminal Bore 225mm diameter 'HDPE bend PN 16
5.1 | 90º | No. | 8
5.2 | 45º | No. | 7
AUXILLIARY WORKS
6 | Valves
6.1 | Supply, install and test Wash outs assembly; with integral isolating valve; fittings and outfall structure Nomial Bore 80 mm and all associated fittings on 225mm dia HDPE pipe as per the drawings. | No. | 4
6.7 | Supply, install and test Air Valves assembly: triple action, anti surge, anti shock, c/w separate female threaded stop cock/isolator and isolating valve, PN 12.5 and all associated fittings on 225mm dia HDPE pipe as per the drawings | No. | 7
6.8 | Supply, install and test branch assembly for offtakes: Fittings to include Gate Valve,Tees, steel pipes in chambers, stub ends and steel flanges on 225mm dia HDPE pipe as per the drawings. | No. | 2
6.7 | Road Crossings
Road Crossings-Murram and Earth
7.1 | Breaking up, Temporary and Permanent Reinstatement of MURRAM road with 300mm thick well graded stabilised gravel with 3% cement content base compacted in layers of 150mm thick using an 8-10 tonne roller to the satisfaction of the Engineer. Contractor to allow for provision of requisite diversion signage, controls and safety precaution in his rates, nominal bore not exceeding 300mm. | m | 12
7.2 | Provide all material and construct concrete ogee pipe sleeve and 150mm thick class 15/20 mass concrete sorround to HDPE pipe under Murram and Earth Road Crossings diameter of pipe n.e. 300mm as per | m | 12
Road Crossings-Tarmac
7.3 | Provide all equipment and materials, excavate below road surface in common material (soil/murram) using trenchless technique.(e.g. Pipe Jacking, horizontal drilling, etc). The rate includes all preparatory works, any requisite shoring, strutting, installation of pipe and pipe casing and necessary grouting and reinstatement, etc. pipe norminal bore n.e.300mm. all works to be executed in close liaison with relevant road authorities and rates to include facillitation of the same. The Bidder to submit Method Statement with Bid for execution of these Works. | m | 6
8 | Anchor and Thrust Blocks
8.1 | Supply all materials and construct 0.3M3 anchor blocks as per drgs and as instructed by the Engineer. | No. | 4
9 | Chambers
9.1 | Provide all materials and construct valve chambers(for AV,WO and Branch chambers) of internal dimensions 1200 x 1200 mm as per the MoWIS standard drawings and the fitting schedule for the specific nodes . Include for supply and fixing of precast concrete cover and step irons, etc as detailed in the drawings and as instructed by the Engineer | No. | 13
10 | Testing
10.1 | Allow for Testing & Flushing of Pipelines and Fittings. Pressure Testing at 1.5 times the pipe pressure rating as per the specifications | M | 4000
11 | Marker Posts
Marker Posts as per Drawings. Provide and install Marker Posts.
11.1 | Marker posts (Pipeline) | Nr. | 10
11.2 | Marker posts (Washout) | Nr. | 7
11.3 | Marker posts (Air Valve) | Nr. | 4
11.4 | Marker posts (Suice Valve) | Nr. | 2
TOTAL INCLUSIVE OF V.A.T FOR PIPELINE CARRIED TO SUMMARY PAGE

## Backwash tank
BILL No. 8
KAHARO - 100m3 ELEVATED TANK
ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
No. |  |  |  | (Kshs) | (Kshs)
1 | Excavation
Excavation shall include strutting,shuttering,stabilizing excavated surface and keeping excavations free of water bailing out, pumping or other means
1.1 | Excavate to reduced levels in top soil for depth not exceeding 0.25 | M3 | 12.6
1.2 | Excavate for tank foundation 0.25-0.5m | M3 | 14.6
1.3 | Ditto but in material other than top soil,rock or hard material depth 0.5-1m | M3 | 14.6
1.5 | Ditto but in rock depth exceeding 1m | M3 | 14.6
Filling
Filling to completed structure including compaction as specified
1.6 | Fill and compact selected excavated material other than top soil,rock or artificially hard material | M3 | 31
Disposal of Excavated Materials
1.7 | Dispose excavated materials other than rock as directed by the Engineer | M3 | 5
1.8 | Dispose excavated material rock or artificially hard materials on site as directed by the Engineer | M3 | 3
2 | In situ Concrete:Provision and placing.
Rate to include for shuttering
Mass concrete Class 15/20
2.1 | Blinding layer 50mm thick | M3 | 1.1
Reinforced Vibrated Concrete Class 30/20 (ready mix)
2.2 | Footing and stub columns for steel columns | M3 | 18.5
Reinforcement
High yield hot rolled ribbed bars BS4449.Rate to include for Supply,delivering,cutting,bending,supporting and securing in concrete.
2.3 | High Yield bars | kg | 2220
3 | 1 No ElevatedSteel Tower
| Supply and erect 12m steel Tower frame as per the drawings and specifications.Plate thickness to be 6.0mm for the tank bottom and first level side panels, 4.5mm thick plates for the second and third levels side panels and 2mm for roof. Include for all bolts,jointing material, protection paint and any other necessary materials. Tank panels to be wire brushed and painted externally with one coat of grey primer and two coats of silver aluminium paint. Internally the panels are painted with two coats of non-toxic black bituminous paint. Touch up paint to be applied at site after erection to cover any marks | Nr | 1
4 | Pressed Steel Tank
| Supply and install pressed steel tank 100m3 capacity complete with roof access hatch,access ladder,float level indicator,pipework and 12m steel Tower frame as per the drawings and specifications.Plate thickness to be 6.0mm for the tank bottom and first level side panels, 4.5mm thick plates for the second and third levels side panels and 2mm for roof. Include for all bolts,jointing material, protection paint and any other necessary materials. Tank panels to be wire brushed and painted externally with one coat of grey primer and two coats of silver aluminium paint. Internally the panels are painted with two coats of non-toxic black bituminous paint. Touch up paint to be applied at site after erection to cover any marks | Nr | 1
TOTAL INCLUSIVE OF V.A.T FOR PIPELINE CARRIED TO SUMMARY PAGE |  |  |  |  | 0