## Sheet1
EQUIPPING OF SAGANA SUB COUNTY BOREHOLE IN NDIA SOUTH CONSTITUENCY - KIRINYAGA COUNTY
TENDER NO: TWWDA/T/029/2022-2023 - EQUIPPING OF 1NO. BOREHOLE
Item No. | Item Description | Unit | Quantity | Rate (KSHS) | Amount (KSHS)
Bill No. 1 | PRELIMINARY AND GENERAL ITEMS
Contractual Requirements
1.1 | Allow for provision of Performance Security and Insurances of works, workmen and third parties in accordance with the General Conditions of Contract | LS | 1
1.2 | Allow Provisional Sum of Kshs 50,000 to cover supervision costs of Engineers assigned on the project from TWWDA head office to cover expenses for communication, transport, allowances etc to be expended as directed by the Project Manager. | PC | 1
1.2.1 | Allow for Contractor's profits and overheads for Bill Item 1.2 above | % | 10
1.3 | Provide and maintain signboard as directed by the Engineer. Rate to be inclusive of removal after completion - location and design to be in accordance with TWWDA standard sign board design drawings and as directed by the Engineer | Nr | 1
Contractor's mobilization and demobilization
1.4 | Mobilization, transportation of machinery, equipment and materials to the site and demobilization on completion | LS | 1
1.5 | Allow for testing and commissioning of works | LS | 1
Total for Preliminary and General Items
Item No. | Item Description | Unit | Quantity | Rate (KSHS) | Amount (KSHS)
Bill No. 2 | Pump installation, Solar panels and Associated structures
2.1 | Pump installation.
2.1.1 | Supply and install Vertical Mounting, Multi Stage, Centrifugal Type Submersible Pump capable of pumping 12.8m³/hr against a Total Head of 130m and pump set at depth of 116m, Coupled with a suitable motor with same ratings with the pump. The entire pump-set body including the strainer, Cable Guard, Non Return Valve, impellers, shaft, Locking Nuts, Washers etc shall be made of heavy duty stainless steel material. The Bearings shall be the Water Lubricated type and wear resistant. The pump should also be suitable for 3 phase 415v and shall be hydraulically and dynamically balanced. The pump shall be GRUNDFOS or approved equivalent subject to approval by the Engineer. The bidder MUST submit adequate technical literature to assist in evaluation. The literature information shall INCLUDE; Performance curves for the pump set, Make, type model and the country of origin of the pump and motor. | Nr | 1
2.1.2 | Supply and install 6mm squared 2.5 core flat submersible cable for the above pump | M | 136
2.1.3 | Heat shrink joint for the above cable | Nr | 1
2.1.4 | 0.75mm square 1 core Blank Electrode cable | M | 136
2.1.5 | 0.75mm square 1 core Brown Electrode cable | M | 136
2.1.6 | Supply and install heavy duty upvc delivery pipes 2½ inch of 3M length made of strong non corroding and deep square thread spigot ends with rubber joint for easy coupling and an assured seal having a safe pulling load of over 4000kgs. The pipe should be Dayliff or the equivalent approved. | Nr | 39
2.1.7 | Mild steel adopter | Set | 1
2.1.8 | Supply and install pvc 3/4 inch class D Airline pipes. | Nr | 20
2.1.9 | Construct borehole headworks cover complete with sundries as indicated in the drawings. | Nr | 1
Sub Total taken to Collection
Item No. | Item Description | Unit | Quantity | Rate (KSHS) | Amount (KSHS)
2.2 | Solar panel installation
2.2.0 | Supply and mount to position solar modules capable of powering the pump set as described in 2.1.1 above. Solar Panels of Minimum 330W polycrystalline or monocrystalline. Bidder MUST submit adequate technical literature to assist in evaluation. The literature information shall include: Make, Type, Model, Certification, Specifications and the Country of origin of the PV Modules | Watts | 10500
2.2.1 | Supply and instal sunverter solar pump control for the above pump. | Nr | 1
2.2.2 | Ditto pv disconnect switch | Nr | 1
2.2.3 | Ditto electrical and installation sundries | Nr | 1
2.2.4 | Ditto 6mm squared 4 core underground cable, Borehole to panel | M | 40
2.2.5 | Ditto 6mm squared 4 core from panel to the main supply | M | 30
2.2.6 | Ditto 1.5mm squared 2 core underground cable electrodes | M | 30
2.2.7 | Ditto 1.5mm squared 2 core underground cable floatswitch | M | 30
2.2.8 | Earth rod coupled with clamp | Nr | 1
2.2.9 | 6mm squared Earth cable | M | 10
2.2.10 | Float switch and cable for the storage tank | Nr | 1
2.2.11 | Borehole 1½ inches water meter i.e kent or equivalent approved | Nr | 1
2.2.12 | Electrodes pencil | Pair | 1
Sub Total taken to Collection
Item No. | Item Description | Unit | Quantity | Rate (KSHS) | Amount (KSHS)
2.3 | Solar panels mounting structure
| Supply and install solar module mounting structure from hot galvanized steel profile, foundation suitable to the dimensions of selected PV modules and PV numbers. The mounting to provide a fixed inclination of the modules minimum 15 degrees with lower side 2.6m above ground level with vertical supports, plates screws and casting concrete foundations. The structure profile includes bracing and double hot galvanized angels for dividers. The mounting structures and the foundations must be suitable to withstand all static loads (weight of the modules, wind loads etc) that might occur according to the site conditions. The mounting structure components are bonded together to guarantee potential equalization. All works and materials must be according to specifications, drawings and supervisor's instructions and approval. | LS | 1
Sub Total taken to Collection
Item No. | Item Description | Unit | Quantity | Rate (KSHS) | Amount (KSHS)
Collection Page for Pump installation, Solar panels and Associated structures
| Sub Total from page 2 |  |  |  | 0
| Sub Total from page 3 |  |  |  | 0
| Sub Total from page 4 |  |  |  | 0
| Total for Pump installation, Solar panels and Associated structures take to Summary |  |  |  | 0
Bill No.3 | BOQ FOR 1 NO STEEL TOWER 12 M HIGH TO CARRY 24M3 CAPACITY HOT DIPPED GALVANIZED PRESSED STEEL WATER TANK
ITEM | DESCRIPTION | Unit | Quantity | RATE (KShs.) | Amount (KSHS)
3.1 | Elevated Water Tank Tower
Excavation shall included strutting, shuttering, stabilizing excavated surface and keeping excavations free of water bailing out, pumping or other means
3.1.1 | Excavate to reduced levels in top soil for depth not exceeding 0.25 | M3 | 3
3.1.2 | Excavate for tank foundation 0.25-0.5 m | M3 | 5
3.1.3 | Ditto but in material other than top soil, rock or hard material depth 0.5-1m | M3 | 5
3.1.4 | Ditto but in material other than top soil, rock or artifically hard depth 1-2 m | M3 | 5
3.1.5 | Ditto but in rock depth 1-2m | M3 | 2
Filling to completed structure including compaction as specified
3.1.6 | Fill and compact selected excavated material other that top soil, rock or artifical hard material | M3 | 2
3.1.7 | Dispose excavated materials other than rock as directed by the Engineer | M3 | 5
Disposal of Excavated Materials
3.1.8 | Dispose excavated material rock or artificicially hard materials on site as dircted by the Engineer | M3 | 2
In situ concrete: Provision and placing. Rate to include for shuttering (Mass concrete Class 15/20)
3.1.9 | Blinding layer 50 mm thick | M3 | 1
Reinforced Vibrated Concrete Class 30/20 (ready mix)
3.1.10 | Footing and stub columns for steel columns | M3 | 6.3
Sub Total taken to Collection
Item No. | Item Description | Unit | Quantity | Rate (KSHS) | Amount (KSHS)
Reinforcement
High yield hot rolled ribbed bars BS4449. Rate to include for supply, delivering, cutting, bending, supporting and securig in concrete
3.1.11 | High Yield bars | Kg | 500
3.2 | 1No. Elevated Tank Tower Supply and erect 12 m high steel tower frame as per the drawings and specifications. Include for all bolts, jointing material, protection paint and any other necessary materials. All stell sections to be wire brushed and painted with one coat of grey primer and two coats of silver aluminium paint. Touch up paint to be applied at site after erection to cover any marks. | Nr | 1
3.3 | Pressed Steel Tank
Supply, deliver and install hot dipped galvanized pressed steel tank 24m3 capacity
3.3.1 | Supply and install hot dipped galvanized pressed steel tank 24 M3 capacity complete with roof access hatch, access ladder with access deck round the tank with balustrading and grillages, float level indicator, pipework on 12 m steel tower frame as per the drawings and specifications. Plate thickness to be 4.0 mm for the tank bottom and first level side panels and 2 mm for roof. Include for all bolts, jointing material, protection paint and any other necessary materials. Tank panels, cover, fasteners/bolts, internal bracings and brackets shall be surface finished by HOT DIP GALVANIZING. Rate to include jointing material. Tank to be BRANDED, TANA WATER WORKS DEVELOPMENT AGENCY (logo, lettering, paint colour specifications to be provided by the Project Manager). | Nr | 1
Sub Total taken to Collection
Item No. | Item Description | Unit | Quantity | Rate (KSHS) | Amount (KSHS)
3.4 | Pipework
These are pipes in the vicinity of the tank, including connecting the inlet pipe to the pumping main
3.4.1 | Supply and fix 65 mm diameter GI class B tank inlet pipe | M | 30
3.4.2 | Supply and fix 65 diameter GI Class B Tank Scour | M | 24
3.4.3 | Supply and fix 65 mm diameter GI Class B tank overflow | M | 12
3.4.4 | Supply and 65 mm diameter GI class B tank outlet | M | 15
Valves and Fittings
3.4.5 | Supply and install DN65 PN10 gate valve for the scour | Nr | 1
3.4.6 | Supply and install DN65 PN10 gate valve for the outlet | Nr | 1
3.4.7 | Supply and fix DN65 90o short radius bend to the tank inlet and outlet | Nr | 5
3.4.8 | Supply and fix DN65 - 90o short radius bend to the tank scour | Nr | 2
Total Taken to Collection
3.5 | Plumbing Works | Unit | Quantity | Rate (KSHS) | Amount (KSHS)
3.5.1 | Supply of all Material, Excavate, lay, test and backfill for 80mm PN10 HDPE in delivery pipe to all distribution points from elevated tank ground level. pipeline including handling and fusing all to the satisfaction of the Supervisor on site. Rate to include all fittings and control valves. | M | 250
3.5.2 | Provide all materials and construct meter chamber of internal dimensions 1200 × 1200 mm X1000mm as per the drawings and the fittings schedule for the specific nodes. Include for supply and fixing of locable steel cover as instructed by the Engineer | Nr. | 1
Total Taken to Collection
Collection for Elevated hot dipped galvanized Pressed Steel Tank 24m3 Capacity and 12 m Steel Tower
Total from Page 5
Total from Page 6
Total from Page 7
Total from Page 8
Bill 3 | Total for Elevated hot dipped Galvanized Pressed Steel Tank 24 m3 Capacity and 12m Steel Tower Taken to Summary
Bill No. 4 | Construction of permanent Pump House and Fencing | Unit | Quantity | Rate (KSHS) | Amount (KSHS)
4.1 | Supply all materials and construct a 2.4M X 2.4M X 2.65M height Pump House. The rate shall include all necessary excavations, foundation, floor slab, walling, reinforced, concrete roof slab, internally and externally plastered, steel door lockable from inside, painting, branding with TWWDA Logo and letters -Tana Water Works Development Agency and all other requisite works including sufficient ventilation all to the satisfaction of the supervisor on site. | LS | 1
4.2 | Excavate for, provide all materials and construct 12 ½ gauge galvanized chain link fencing tied to 4 lines through post with 2.1m high 100mmx100mm concrete post above ground level, at 3.0M centers mortised and set 0.9m below ground in mass concrete C15 (1:3:6) surround, including concrete straining posts at corners and at 30m intervals. Concrete posts to have 500mm long cranks at the top and 4 No. 12 ½ gauge barbed wire tied to crank. The rate to include for all excavations and disposal. | M | 120
4.3 | Provide all materials and fabricate a double leafed 38mm x 38mm x 3mm metal framed steel gate overall size 4m wide x 2m high complete with all necessary iron mongery assembled all hinged to 75mm x 75mm x 5mm hollow section steel post capped at the top with 3mm mild steel plate and mortised in concrete surround, with and including gloss crown paint work all at the Engineers direction. | LS | 1
Total for Pump House and Fencing.
BILL SUMMARY
Bill No.1: Preliminary and General Items
Bill No.2: Pump installation, Solar panels and Associated structures
Bill No.3: Storage Tank, Support Structure and Plumbing Works
Bill No. 4: Pump House and Fencing
Sub-Total
Allow 5% Contingencies ……………………………………………………………
Allow 16% VAT……………………………………………………………………….
Grand Total Taken to Form of Tender ……………………………………………