## Grand Summary
TETU - AGUTHI PROPOSED WATER SUPPLY PROJECT
GRAND SUMMARY
SECTION | DESCRIPTION |  | TOTAL AMOUNT
(Kshs.)
1 | PRELIMINARIES & GENERAL (BILL No. 1)
2 | NEW 10,000M3 TETU TREATMENT PLANT
3 | RAW WATER GRAVITY MAIN
4 | INTAKE
5 | ASBESTOS PIPES REMOVAL, REPLACEMENT AND DISPOSAL
6 | 3 NR BPT TANKS ALONG MAINLINE
| Bills Total Exclusive of VAT | (A)
| Add 10%of (A) for Contingencies | (B)
| Bill Total Inclusive of Contingencies | (C)
| Value Added Tax (VAT) - 16% of (C) | (D)
GRAND TOTAL CARRIED TO LETTER OF BID [(C) + (D)]

## P & G BILL
TETU-AGUTHI WATER SUPPLY PROJECT
BILL No. 1
PRELIMINARIES AND GENERAL
ITEM | DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
No. |  |  |  | (Kshs) | (Kshs)
1 | CONTRACTUAL REQUIREMENTS
1.1 | Allow for provision of Performance Security | Item | L.S
1.2 | Allow for provision of contractor all risk insurance | Item | L.S
2 | SPECIAL REQUIREMENTS
2.1 | Contractor's Camp and Storage Yard: Allow for erection of the Contractor's Camp(s), Offices, Storage Yard and other facilities including mobilization, demobilization and movement of the works site on Completion. Include for all equipment, temporary measures, machines, tools, materials, facilities for workers, water and electricity supply etc. all as specified for execution of the Works, for the entire Contract Period. The Employer has no available land to offer for Contractor's Camp, storage of materials and preparation of concrete etc. Identification and procurement of suitable area of land for Contractor's Camp whether rented or purchased is the responsibility of the Contractor. Details of proposed camp / stores, location of land where the Contractor will establish his camp(s) to be submitted with the Bid. | Item | L.S
2.2 | Allow a provisional sum of Kshs.100,000 for utilisation under schedule of dayworks for labour | Item | Sum
2.3 | Add …….% for profit, administration, attendance upon, overheads, etc. for Item 2.2 above | % | 100000
2.4 | Allow a provisional sum of Kshs.1,000,000 for utilisation under schedule of dayworks for materials | Item | Sum
2.5 | Add …….% for profit, administration, attendance upon, overheads, etc. for Item 2.4 above | % | 1000000
2.6 | Allow a provisional sum of Kshs.800,000 for utilisation under schedule of dayworks for lease of major equipment and plants power rating will be provided by the contractor but shall not be less than what is specified in this contract. Any item or major plant employed upon dayworks which has a power rating lower than specified shall be paid for at rates lower than those in the schedule of dayworks. The reduction in rate payable shall be in proportion to the reduction in power rating below that specified above. | Item | Sum
2.7 | Add …….% for profit, administration, attendance upon, overheads, etc. for Item 2.6 above | % | 800000
2.8 | Allow a PC sum of Ksh. 5,000,000 for land and wayleave acquisition and acquisition of all relevant permits and licences from relevant bodies including WRA, NEMA, KENHA, KERRA, KURA, KFS etc. | Item | P.C
2.9 | Add …….% for profit, administration, attendance upon, overheads, etc. for Item 2.8 above | % | 5000000
2.1 | Allow a P.C. Sum of Kshs.500,000 for training of Water service utility Staff during Construction, Testing and Commissioning of the Works | Item | P.C
2.11 | Add …….% for profit, administration, attendance upon, overheads, etc. for Item 2.10 above | % | 500000
2.12 | Allow a PC sum of Ksh. 100,000 for obtaining Metrological data during the project implementation. | Item | P.C
2.13 | Add …….% for profit, administration, attendance upon, overheads, etc. for Item 2.12 above | % | 100000
2.14 | Test Running of the Scheme: Allow for Test Running all the Project Components upon completion for a period of 12 weeks upon completion and offical commissioning of the Works. Test Running to be carried out in close liaison with the Water Services Provider's Staff The Contractor to allow for 'on job' training of Operation and Maintenance Staff, Tools, Chemicals, etc, and ensure that the operations are carried out full time on a 24 hour basis. | Item | L.S
2.15 | Allow for provision of Operation and Maintenance (O&M) Manuals | Item | L.S
2.16 | Allow for provision of As-Built Drawings | Item | L.S
PAGE TOTAL CARRIED FORWARD TO BILL COLLECTION SHEET
3 | SPECIFIED REQUIREMENTS
Sign Boards
3.1 | Allow for provision, erection and maintenance of Project Sign Boards at the sites indicated by the Engineer's Representative, within the Project Area . The rate quoted by the Contractor to include for payment of all statutory charges to the relevant Authority and removal after completion of the Project. | Nr | 4
Setting Out & Survey Work
3.2 | Allow a Provisional Sum of Kshs.200,000 for establishment of Level Survey Datum, Setting Out of the Works. | Item | P.S
The Setting Out / Survey Work including production of Survey Drawings to an agreed scale will be for the following Project Components:
i) Topographic Survey of Intake Works at 10m grid intervals including preparation of updated Layout Plan with contours at 0.5m interval, approximate area 0.5ha.
ii) Engineering Survey of Raw Water Main including preparation of updated plan and profile, approximate length 17km
iii) Topographic Survey of Proposed Water Treatment Works Sites at 10m grid intervals including preparation of updated Layout Plan with contours at 0.5m interval, approximate area 3.5ha.
3.3 | Add …….% for profit, administration, attendance upon, overheads, etc. for Item 3.2 above. | % | 0
PAGE TOTAL CARRIED FORWARD TO BILL COLLECTION SHEET
Office for the Senior Resident Engineer
3.4 | Provide all materials and construct Offices for use of the Senior Resident Engineer including maintenance, water supply, sewerage, drainage, chain link fence, gate, car park, rainwater harvesting tank (5,000 litres with concrete plinth, rainwater gutters, etc), electrical supply, telephone, 24 hour security and other facilities for the Senior Resident Engineer, all as specified (Building, furniture and equipment to revert to Employer). Include for all water borne sanitation waste pipes, inspection chambers, Septic Tank etc. Include for KPLC Power Supply with a Meter Board. Building to be constructed using permanent building materials as per Ministry of Public Works Building By-laws or approved equivalent. Note: This is to be carried out as Priority Works within the first 16 Weeks after date of Commencement of Works. Floor area not exceeding 220m2 | Item | L.S
3.5 | Allow for provision of Rented or Pre-fab Offices for Senior Resident Engineer's Staff during the first 16 Weeks of the Contract Period as per Clause 101 of the General and Specific Specifications of Bid Document Volume II. Offices to include 3 Nr Offices, Conference Room, Tea Room, W.C and Parking Space for at least 3 Nr Vehicles. Include for provision of 24 hour security, water, sewerage, electricity, etc. Note: If Construction of the RE's Offices under Items 3.4 above is delayed beyond the first 16 weeks of the Contract Period, the Contractor shall be liable to provide rented or Pre-fab offices for any additional period at his own cost | Month | 6
3.6 | Provisional Sum of Ksh. 500,000 for provision of furniture and equipment for the Senoir Resident Engineer's Offices. Final List of Furniture & Equipment to be procured will be provided by the Senior Resident Engineer prior to commencement of Works. The furniture and equipment to revert to the Employer at the end of the Contract. | Item | P.S
3.7 | Add …….% for profit, administration, attendance upon, overheads, etc. for Item 3.6 above. | % | 0
3.8 | Maintenance and attendance of the Senior Resident Engineer's Office. Contractor to include for supply of consumables. Note: Contractor to price for the monthly requirement of stationery, cleaning materials and other consumables specified in the Specifications. | Month | 12
3.9 | Provision and maintenance of 1nr. RTK Conmav N5 GNSS receiver and rover set with all relevant accessories including requisite software, RTK FIX T1 data collector Survey Equipment and 1nr Carlson CR+ model robotic total station inclusive of all relevant accessories as shall be directed by the engineer for the sole use of the Senior Resident Engineer during the duration of the Contract. Equipment to revert to the employer at the end of the Contract. | Item | L.S
PAGE TOTAL CARRIED FORWARD TO BILL COLLECTION SHEET
Senior Resident Engineer's Staff
Provide the following Staff for the Senior Resident Engineer's Office. (Note: The Staff to be employed by the Contractor but to be under the exclusive day to day instruction of the Senoir Resident Engineer). The rate to include for all overtime, acccomodation costs, requisite Governmet of Kenya mandotary deductions, etc. all neccesary for the Staff to perform their duties. The minimum relevant experience for the Staff should be at least 5 years
3.1 | Drivers (1Nr. x 12 Months each) | Month | 24
Vehicles
3.11 | Allow a P.C. Sum of KShs.4,000,000 for supply of 1Nr. (One) 4WD Vehicles, 1Nr. (One ) Fortuner or approved equivalent, including road licenses, number plates, insurances, etc. The vehicle to revert to Employer after completion of Contract. Minimum specifications include but not limited to the following: • Engine - 3.0 litres Turbo DieselOne | Item | P.C
3.12 | Add …….% for profit, administration, attendance upon, overheads, etc. for Item 3.11 above. | % | 0
PAGE TOTAL CARRIED FORWARD TO BILL COLLECTION SHEET
3.13 | Allow a P.C. Sum of Kshs. 250,000 for supply of 1 Nr. 200 cc Motorbike, including road licence, number plate insurances, 1 set of crash helmet, 1 set of gloves, etc.The motorbike to revert to the Employer after completion of the Contract. Minimum specifications include but not limited to the following: • Ignition – capacitor Discharge (CDI) • Starter – Primary Kick • Displacement – 175cc • Transmission – 5 speed • Final Drive – Roller Chain • Fuel capacity 7 litres to 10 litres • Braking system – front/rear – trailing drum • Engine – Air cooled, 2 strokes, single cylinder. | Item | L.S
3.14 | Add ……% for profit, administration, attendance upon, overheads, etc for item 3.13 above. | % | 0
3.15 | Allow a P.C. Sum of KShs. 200,000 for maintaining, running and servicing the above Vehicles and Motorbikes all as specified, including all costs of transfer to the Employer at the end of Contract, insurance, road licences etc. | Item | P.S
3.16 | Add….% for profit, administration, attendance upon overheads etc for Item 3.15 above. | % | 0
Telecommunications
3.17 | Provisional a P.C. Sum of Kshs. 400,000 for provision of communication facilities and services (telephone, email, fax, postal, courier services, etc.) for the Project / Site Offices and the Supervision Staff. | Item | P.C
3.18 | Add …….% for profit, administration, attendance upon, overheads, etc. for Item 3.17 above. | % | 0
Electrical Works
3.19 | Allow a P.C. Sum of Kshs. 1000000 for installation of power and all subsequent electrical works within Treatment works site. | Item | P.C
3.2 | Add …….% for profit, administration, attendance upon, overheads, etc. for Item 3.19 above. | % | 0
Employer's Counterpart Staff Costs
3.21 | P.C. Sum of Kshs. 1000000 to cover costs of the Employer's Counterpart Staff assigned to the Project including transport, communication, allowances, etc. | Item | P.C
3.22 | Add …….% for profit, administration, attendance upon, overheads, etc. for Item 3.21 above. | % | 0
PAGE TOTAL CARRIED FORWARD TO BILL COLLECTION SHEET
Other Costs
3.23 | Allow a P.C. Sum of Kshs. 1000000/ for Payments demanded by the Authorities for re location of existing services (water pipelines, sewer liners power cable telcom cables etc), Road crossings, microtunnellings, etc., including any statutory levies to relevant Authorities. Liaison with the relevant Authorities shall be the responsibility of the Contractor for the timely execution of the Works. | Item | P.C
3.24 | Add …….% for profit, administration, attendance upon, overheads, etc. for Item 3.23 above. | % | 0
3.25 | Allow a P.C. Sum of Kshs. 150,000 for Inspection and Witness Testing of Pipes, Fittings and Equipment at manufacturer's premises by the Employer, Engineer and their representatives | Item | P.C
3.26 | Add …….% for profit, administration, attendance upon, overheads, etc. for Item 3.25 above. | % | 0
3.27 | Allow a P.C. Sum of Kshs.75,000/ for Third Party Inspection of Pipes, Fittings, Equipment, etc during Manufacture and Construction Works.
3.28 | Add …….% for profit, administration, attendance upon, overheads, etc. for Item 3.27 above. | % | 0
3.29 | Allow a P.C. Sum of KShs.500000 to be used as directed by the Engineer. | Item | P.C
3.3 | Add …….% for profit, administration, attendance upon, overheads, etc. for Item 3.29 above. | % | 0
3.31 | Allow a Provisional Sum of Kshs.300000 for carrying out cadastral survey by licenced Surveyor including obtaining approval by Director of Surveys and issuance of Title Deeds at various Project sites, or for any requisite Engineering Survey, as directed by the Engineer. | Item | P.C
3.32 | Add …….% for profit, administration, attendance upon, overheads, etc. for Item 3.32 above. | % | 0
4 | SPECIFIC CONDITIONS
4.1 | Allow for all specific works related to working along active pipelines and maintaining continuity of water supply including protection of supports etc. of existing pipelines during construction activity. | Item | L.S
4.2 | Allow for all Specific Works related to working within active Water Treatment Works, Pumping Stations and Storage Reservoir Sites and keeping the existing Facilities fully operational. If disruption of raw water or treated water may occur for whatever reason, the Contractor to recticfy the situation within 12 hours in order to keep the works fully operational. | Item | L.S
PAGE TOTAL CARRIED FORWARD TO BILL COLLECTION SHEET
5 | OTHER WORKS OBLIGATIONS
5.1 | Allow for any costs associated with compliance with Environmental, Health and Safety Requirements, the Environmental and Social Management and Monitoring Plan (ESMMP) as required by Government Agencies and Prevailing Legislation. | Item | L.S.
5.2 | The Contractor shall describe in detail hereunder other works, obligations and things which may be referred to in the Specifications or which he may consider to have been omitted from the Bills of Quantities and for which he desires to enter a separate charge (the charge to be carried direct to the amount column). FULL DESCRIPTION OF ITEM(S) OF WORK OR ANY OTHER ISSUE SHOULD BE MADE. If no separate charge is made hereunder, the rates in the Bills of Quantities will be held as covering all expenses for all such Works. | Item | L.S.
PAGE TOTAL CARRIED FORWARD TO BILL COLLECTION SHEET

## Collection Sheet 1
TETU-AGUTHI WATER SUPPLY PROJECT
BILL No. 1.1
Totals Collection sheet
Amount
(Kshs)
Page Total, Page 1 of 7
Page Total, Page 2 of 7
Page Total, Page 3 of 7
Page Total, Page 4 of 7
Page Total, Page 5 of 7
Page Total, Page 6 of 7
Page Total, Page 7 of 7
Section 1 Total Exclusive of VAT Carried to The Bill of Quantities Grand Summary

## Section 1 Summary Sheet
SECTION 1
PRELIMINARIES AND GENERAL (BIL No. 1.1)
SUMMARY SHEET
Amount
(Kshs.)
Bill No. 1.1 - Preliminaries and General
Section 3 Total Exclusive of VAT Carried to The Bill of Quantities Grand Summary

## Flocculation basin
TETU-AGUTHI WATER SUPPLY PROJECT
BILL No. 3.1
TREATMENT WORKS - STILLING WELL, CHEMICAL DOSING CHANNEL & FLOCCULATION BASIN
ITEM | DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
No. |  |  |  | Kshs | KShs. | cts
1 | STILLING WELL
1.1 | Excavation
The rates shall include for all strutting, shuttering, stabilising the excavation faces and keeping the excavation free of water by pumping, bailing or other means
Excavate for foundations, part backfill after construction and remainder, cart away to tips or use as fill on site, all as directed by the Engineer
1.1.1 | Maximum depth n.e. 1.0 m | m3 | 16
1.1.2 | -Ditto - for depth 1 - 2 m | m3 | 8
1.1.3 | Extra over Item 1.1.1 & 1.1.2 for excavation in rock Class 'A', blasting not permitted (Provisional) | m3 | 2
1.1.4 | -Ditto- for excavation in rock Class 'B', blasting not permitted (Provisional) | m3 | 3
1.1.5 | -Ditto- for excavation in rock Class 'C', blasting not permitted (Provisional) | m3 | 1
1.2 | Concrete Works
Provide, mix and place concrete as directed
1.2.1 | Plain concrete Class 15/20 in 75mm blinding layer under combined column base | m3 | 1
1.2.2 | Ditto-but for Stilling Well base slab | m3 | 1
Vibrated, reinforced concrete class 25/20 in:-
1.2.3 | Combined Column base | m3 | 2
1.2.4 | Columns | m3 | 1
1.2.5 | 200mm thick base slab | m3 | 3
1.2.6 | 200mm thick R.C walls | m3 | 7
1.2.7 | 150mm thick R.C baffle walls | m3 | 2
1.3 | Reinforcement
Provide and fix high tensile steel reinforcement to SRN 127 including cutting, bending, propping, with spacers and tying as specified
1.3.1 | Reinforcement, all diameters | kg | 2500
PAGE TOTAL CARRIED TO SECTION COLLECTION SHEET
1.4 | Formwork
Provide and fix shuttering including propping, strutting and striking all as specified
(i) Vertical Formwork - Class F1 Finish
1.4.1 | Vertical sides of Column bases, width n.e 0.3m | m | 16
(ii) Vertical Formwork - Class F3 Finish
1.4.2 | Vertical sides of Columns-width n.e 0.3m | m | 12
1.4.3 | Sides of 200mm thick base slab | m | 14
1.4.4 | Outer faces of stilling well walls-width n.e 4.2 m | m2 | 53
1.4.5 | Inner faces of the stilling well walls-width n.e 4.2 m | m2 | 46
1.4.6 | Sides of the baffle wall in stilling well | m2 | 18
(i) Horizontal Formwork - Class F3 Finish
1.4.7 | Soffit of baffle wall in stilling well, width n.e 0.15m | m | 4
Other Formwork
1.4.8 | Boxing out for Pipes in 200mm thick R.C. Walls for Stilling Well pipe diameters n.e. 350mm and making good after pipe inserts installation | Nr | 1
1.4.9 | Ditto for pipe diameter n.e 150mm | Nr | 2
1.4.10 | Boxing out for Chemical dosing channel-12045mm x 800mm and making good after construction of chemical dosing channel | Nr | 1
1.5 | Concrete Surface Finish
1.5.1 | Provide Class UF3 Finish for top of base slab of stilling well | m2 | 9 |  |  | 11.56
1.6 | Construction Joints
Provide and install the following waterstops in construction joints including all surface treatment, formwork, forming of rebate 20mm x 20mm and sealing of rebate with polysulphide sealant all as per Drawings and Specifications.
1.6.1 | 200mm wide expandite super-cast water foil PVC or similar approved waterstop in construction joints in walls. | m | 26 |  |  | 13.6
PAGE TOTAL CARRIED TO SECTION COLLECTION SHEET
1.7 | Metalwork
All steel work to be completely cleaned by acid dipping prior to galvanising
1.7.1 | Provide and fix Upvc coated cast irons steps in stilling well | Nr | 14
1.8 | Leak Proof Testing
1.8.1 | Allow for leak proof testing of Stilling Well as specified | Item | L.S
1.9 | Pipework Fittings & Valves
Supply, Transport to Site, install, test and commission Including Jointing Material, Bolts, Gaskets, Packing, Jointing Glue, etc, As Applicable
Raw Water Gravity Main Pipework - Approved Lined Ferrous Pipes
1.9.1 | 400mm dia. Flanged spigot 900 bend (Mark 1) | Nr | 1
1.9.2 | 400mm dia. Double flanged pipe with puddle flange at 400 mm from the flanged end,length 800mm (Mark 2) | Nr | 1
1.9.3 | 400mm dia. All flanged 900 bend (Mark 3) | Nr | 2
1.9.4 | 150mm dia. flanged spigot pipe 2600mm long (cut to suit on site) (Mark 4) | Nr | 1
1.9.5 | 400mm dia. flange adaptor (Mark 5) | Nr | 2
1.9.6 | 400mm dia. flanged pipe 1200mm long (Mark 6) | Nr | 1
1
1.9.7 | 400mm dia. Flanged gate valve with an extension spindle 1.5 m long (Mark 7) | Nr | 1 |  |  | kisii bill 4.6
1.9.8 | 400mm dia. Flanged spigot pipe 1200mm long (Mark 8) | Nr | 1
Recirculation Pipework - Approved Lined Ferrous Pipes
1.9.9 | 150mm dia. Flanged 900 bend with plain end beveled (Mark a) | Nr | 1
1.9.10 | 150mm dia. Double flanged pipe with puddle flange at 400 mm from the flanged end,length 800mm (Mark b) | Nr | 1
1.9.11 | 150mm dia. All flanged 900 bend (Mark c) | Nr | 2
1.9.12 | 150mm dia. flanged spigot pipe 3650mm long (cut to suit on site) (Mark d) | Nr | 1
1.9.13 | 150mm dia. flanged adaptor (Mark e) | Nr | 1
1.9.14 | 150mm dia. flanged spigot pipe 1200mm long (Mark f) | Nr | 1
1.9.15 | 150mm dia. coupling (Mark g) | Nr | 1
PAGE TOTAL CARRIED TO SECTION COLLECTION SHEET
Sour Pipework - Approved Lined Ferrous Pipes
1.9.16 | 150mm dia. flanged spigot 900 bend with puddle flange at 100 m from plain end (Mark וֹ) | Nr | 1
1.9.17 | 150mm dia flanged adaptor (Mark וֹi) | Nr | 2
1.9.18 | 150mm dia flanged 900 bend (Mark וֹוֹוֹ) | Nr | 2
1.9.19 | 150mm Flanged spigot pipe cut to suit on site,length 1200 (Mark iv) | Nr | 1
1.9.20 | 150mm dia Gate valve with extension spindle 1.5m long (short face) with a T-key for operation (Mark v) | Nr | 1
1.9.21 | 150mm dia Flanged spigot pipe cut to suit on site,length 6745 (Mark vi) | Nr | 1
2 | CHEMICAL DOSING CHANNEL & DOSED WATER CHANNEL
2.1 | Concrete Works
Provide, mix and place concrete as directed
Vibrated Reinforced Concrete Class 25/20 in:-
2.1.2 | Base slab of channel | m3 | 4
2.1.3 | Walls of channel | m3 | 9
2.2 | Reinforcement
Provide and fix high tensile steel reinforcement to SRN 127 including cutting, bending,propping, with spacers and tying as specified
2.2.1 | Reinforcement, all diameters | kg | 1560
2.3 | Formwork
Provide and fix shuttering including propping, strutting and striking all as specified
(ii) Vertical Formwork - Class F3 Finish
2.3.1 | Sides of 200mm thick channel base slab | m | 25
2.3.2 | Walls of channel - width n.e. 0.1n | m | 49
2.3.3 | External walls of channel - width n.e. 2.0m | m2 | 30
2.3.4 | Internal walls of the channel - width n.e. 2.0m | m2 | 29
2.3.5 | Vertical sides of the wall-width n.e 0.3 | m | 1
2.3.6 | Ditto for-width n.e 0.2 | m | 1
PAGE TOTAL CARRIED TO SECTION COLLECTION SHEET
Other Formwork
2.3.7 | Allow for 75mm x 75mm rebate in walls of dosed water channel for cover slabs | m | 48
2.3.8 | Boxouts for Pipes in 200mm thick R.C. Walls for chemical dosing pipe diameter n.e 150 and making good after pipe inserts installation | Nr | 1
2.4 | Concrete Surface Finish
2.4.1 | Provide Class UF3 Finish for top of base slab of channel | m2 | 21 |  |  | 20.811
2.5 | Construction Joints - Water Bar
Provide and install the following waterstops in construction joints including all surface treatment, formwork, forming of rebate 20mm x 20mm and sealing of rebate with polysulphide sealant all as per Drawings and Specifications
2.5.1 | 200mm wide expandite super-cast water foil PVC or similar approved waterstop in vertical construction joints in walls | m | 32
2.6 | Metal Work
All steelwork to be completely cleaned by acid dipping prior to galvanizing
2.6.1 | Provide and fix GMS open mesh cover with frame size 0.8m x 0.95m, to dosing channel. Include for provision and fixing of fish tailed lugs into concrete walls. | Nr | 1
2.6.2 | Ditto-but frame size 0.3 m x 0.95 m | Nr | 1
2.6.3 | Ditto-but frame size 0.8 m x 0.95 m | Nr | 1
2.6.4 | Provide and fix GMS support bracket for GMS open mesh cover. Include for all materials (M.S. angle, plate, bolts, etc) and necessary drilling and fixing to concrete wall as required. | Nr | 3
2.6.5 | Provide and fix 900 mm high level balustrades of 40 mm diameter tubing Class B throughout, consisting of handrail and parallel middle rail 450 mm below the hand rail with balusters at maximum 1500 mm centres. | m | 50
2.6.6 | Provide and fix 750mm wide steel access staircase to chemical dosing channel. | Nr | 1
2.7 | Miscellaneous
2.7.1 | Supply & fix Measuring Gauge | Nr | 1
2.7.2 | Supply & fix thin plate measuring weir | Nr | 1
2.8 | Precast Concrete Walkway Slabs
Precast concrete Class 25/20 finished fair on all surfaces and reinforced as shown on the drawings. Provide and fix:-
2.8.1 | 75mm thick cover slab size 950mm x 400mm wide including 2Nr. Mild steel key holes cast with slab for dosed water channel | Nr | 60
PAGE TOTAL CARRIED TO SECTION COLLECTION SHEET
3 | FLOCCULATION BASIN
3.1 | EARTHWORKS
EXCAVATION
The rates shall include for all strutting, shuttering, stabilising the excavation faces and keeping the excavation free of water by pumping, bailing or other means
Bulk excavations and top soil stripping for all structures are measured under Bill No. 20 (Site & Ancillary Works).
Excavate below stripped level to formation level in common material, part backfill after construction and remainder, cart away to tips or use as fill on site, all as directed by the Engineer.
3.1.1 | Maximum depth n.e. 1.0 m | m3 | 392
3.1.2 | Ditto- but depth 1m-2m | m3 | 245
3.1.3 | Extra over Items 1.1.1 to1.1.2 for excavation in rock Class 'A', blasting not permitted (Provisional) | m3 | 6
3.1.4 | -Ditto- for excavation in rock Class 'B', blasting not permitted (Provisional) | m3 | 9
3.1.5 | -Ditto- for excavation in rock Class 'C', blasting not permitted (Provisional) | m3 | 4
FILL
3.1.6 | Transport approved excavated material from site stock pile and use as fill. Compact in 200mm thick layers,making up levels under floccuation bassin base slab as directed by the Engineer. Compaction tests to be done for each layer as directed by the Engineerand to be included in the contractor's rates. | m3 | 50
3.1.7 | Provide, lay and level out the crushed stone, sand or gravel blinding 50mm thick to surface of filling, including watering and rolling to achieve satisfactory compaction. | m2 | 6
3.2 | CONCRETE WORKS
Provide, mix and place concrete as directed
3.2.1 | Plain concrete Class 15/20 in 75mm blinding layer under under retaining walls strip footing | m3 | 8
3.2.2 | Plain concrete Class 15/20 in 75mm blinding layer under base slab of the flocculation basin | m3 | 15
Vibrated, Reinforced concrete Class 25/20 in:-
3.2.3 | Retaining walls Strip footing | m3 | 37
3.2.4 | Flocculation basin base slab | m3 | 51
3.2.5 | Walls | m3 | 36
3.2.6 | Tie Beams | m3 | 3
PAGE TOTAL CARRIED TO SECTION COLLECTION SHEET
Precast concreteclass 25/20 in:-
3.2.7 | Provide and fix precast concrete Baffle walls each150mm thick; 9.85m long ; depth ranging between 1.55m - 1.66m finished fair on all faces. | Nr | 22
3.2.8 | Ditto but 9.75m long ; depth ranging between 1.55m -1.66m | Nr | 12
3 | REINFORCEMENT
Provide and fix high tensile steel reinforcement to SRN 127 including cutting, bending, propping, with spacers and tying as specified
3.1 | Reinforcement, all diameters | kg | 20000
3.4 | FORMWORK
Provide and fix shuttering including propping, strutting and striking all as specified
(i) Vertical Formwork - Class F1 Finish
3.4.1 | Sides of 400mm thick retaining wall footing | m | 138
3.4.2 | Sides of wall, width n.e 0.1m kicker | m | 142
3.4.3 | Walls below floor level | m2 | 283
3.4.4 | Inner faces of walls above floor level | m2 | 68
(ii) Vertical Formwork - Class F3 Finish
3.4.5 | Sides of 250mm thick sloping base slab - (1 in 45 slope) | m | 63
3.4.6 | Sides of walls-width n.e 0.1m kicker | m | 142
3.4.7 | Inner faces of walls above finished ground level | m2 | 77
3.4.8 | Walls above finished ground level | m2 | 117
3.4.9 | Tie beam width n.e 0.2 m | m | 41
(iii) Horizontal Formwork - Class F1 Finish
3.4.10 | Soffit of the tie beam-width n.e 0.75m | m | 22
(iv) Horizontal Formwork - Class F1 Finish
3.4.11 | Sloping sides of cantilever support for headstock | m2 | 2
(v) Other Formwork
3.4.12 | Boxouts for Pipes in 300mm thick R.C. Walls for scour pipe diameter n.e. 150mm and making good after pipe inserts installation | Nr | 2
3.4.13 | Boxouts for 600mm x 1000mm inlet control penstock in 300mm thick RC wall and making good after installation of the penstocks | Nr | 2
3.4.14 | Boxouts for 600mm x 1300mm outlet control penstock in 300mm thick RC wall and making good after installation of the penstocks | Nr | 2
PAGE TOTAL CARRIED TO SECTION COLLECTION SHEET
3.5 | CONCRETE SURFACE FINISH
3.5.1 | Provide Class UF3 Finish for top of base slab of basin | m2 | 198
3.6 | CONSTRUCTION JOINTS
Provide and install the following waterstops in construction joints including all surface treatment, formwork forming of rebate and sealing of rebate with polysulphide sealant all as per Drawings and Specification
3.6.1 | 200mm wide expandite super-cast water foil PVC or similar approved waterstop in construction joints in walls (Provisional) | m | 73
3.7 | LEAK PROOF TESTING
3.7.1 | Allow for leak proof testing of Flocculation Basin as specified | Item | L.S
3.8 | PIPEWORK, FITTINGS & VALVES
Supply, Transport to Site, install, test and commission including Jointing Material, Bolts, Gaskets, Packing, Jointing Glues, etc as Applicable.
3.8.1 | Special 600mm x 1000mm opening inlet control penstock with extended spindle and headstock (non-rising stem type) (Hambaker or approved equivalent). | Nr | 2
3.8.2 | Special 600mm x 1300mm opening outlet control penstock, non-rising stem type with extended spindle (Hambaker or approved equivalent) | Nr | 2
Sour Pipework - Approved Lined Ferrous Pipes
3.8.3 | 150mm dia. flanged spigot pipe 600mm long with puddle flange at 150mm from plain end (Mark i) | Nr | 2
3.8.4 | 150mm dia all flanged 90 bend (Mark j) | Nr | 5
3.8.5 | 150mm dia flanged spigot pipe cut to suit on site, length 1000mm (Mark k) | Nr | 1
3.8.6 | 150mm dia flanged adaptor (Mark l) | Nr | 4
3.8.7 | 150mm Flanged spigot pipe cut to suit on site,length 3200 mm(Mark m) | Nr | 1
3.8.8 | 150mm dia Gate valve with extension spindle 1.2m long (short face) with a T-key for operation (Mark n) | Nr | 2
3.8.9 | 150mm Flanged spigot pipe cut to suit on site,length 3300mm (Mark o) | Nr | 1
3.8.10 | 150mm Flanged spigot pipe cut to suit on site,length 825mm (Mark p) | Nr | 1
3.8.11 | 150mm dia Flanged spigot 900 bend (Mark q) | Nr | 1
PAGE TOTAL CARRIED TO SECTION COLLECTION SHEET
3.9 | MISCELLANEOUS
3.9.1 | Provide all materials and fix GMS CAT ladder, length n.e 1.7m to Flocculation Basin 1 | Nr | 1
3.9.2 | Provide and apply Epoxy wall and floor coating, "MASTERTOP 1110T" or approved equivalent on internal surfaces of walls and floor of Flocculation Basin. | m2 | 1000
4 | FLOCCULATED WATER CHANNEL
4.1 | CONCRETE
Provide, mix and place concrete as directed
4.1.1 | Plain concrete Class 15/20 in 75mm blinding layer under Flocculated water Channel | m2 | 12
Vibrated, Reinforced concrete Class 25/20 in
4.1.2 | Walls | m3 | 5
4.1.3 | Channel Slab | m3 | 4
4.2 | REINFORCEMENT
Provide and fix high tensile steel reinforcement to SRN 127 including cutting, bending, propping, with spacers and tying as specified
4.2.1 | Reinforcement, all diameters | kg | 1080
4.3 | FORMWORK
Provide and fix shuttering including propping, strutting and striking all as specified
(i) Vertical Formwork - Class F1 Finish
4.3.1 | Sides of 200mm thick slab | m | 16
4.3.2 | walls width n.e 0.1m kicker | m | 14
4.3.3 | walls width n.e 1.6 m | m2 | 23
(ii) Vertical Formwork - Class F3 Finish
4.3.4 | walls width n.e 0.1m kicker | m | 13
4.3.5 | walls width n.e 1.6 m | m2 | 23
4.4 | CONCRETE SURFACE FINISH
4.4.1 | Provide Class UF3 Finish for top of base slab of flocculated water channel | m2 | 8
PAGE TOTAL CARRIED TO SECTION COLLECTION SHEET
4.5 | Metal Work
All steelwork to be completely cleaned by acid dipping prior to galvanizing
4.5.1 | Provide all materials and fix GMS CAT ladder, length n.e 1.7m to Flocculated Water Channel. | Nr | 1
4.5.2 | Provide and fix GMS open mesh cover with frame size 1.65m x 0.75m, to flocculated water channel. Include for provision and fixing of fish tailed lugs into concrete walls. | Nr | 1
4.5.3 | Provide and fix 900 mm high level balustrades of 40 mm diameter tubing Class B throughout, consisting of handrail and parallel middle rail 450 mm below the hand rail with balusters at maximum 1500 mm centres. | m | 13
4.6 | Precast Concrete
Precast concrete Class 25/20 finished fair on all surfaces and reinforced as shown on the drawings. Provide and fix:-
4.6.1 | 75mm thick cover slab size 1250mm x 400mm wide including 2Nr. Mild steel key holes cast with slab for dosed water channel | Nr | 14
5 | CHAMBERS
5.1 | Provide all materials and construct a concrete Valve Chamber, internal dimensions 1200x1200mm. Include for supply and fixing of precast concrete cover slab and step irons, as detailed on Standard Drawing depth n.e 2.1 m | Nr | 1
5.2 | Provide all materials and construct a concrete Scour Chamber, internal dimensions 1200x1200mm. Include for supply and fixing of precast concrete cover slab and step irons, as detailed on Standard Drawing depth n.e 2.1 m | Nr | 1
PAGE TOTAL CARRIED TO SECTION COLLECTION SHEET

## Collection Sheet 3.1
TETU-AGUTHI WATER SUPPLY PROJECT
BILL No. 3.1
PAGE TOTALS COLLECTION SHEET
Amount
Kshs.
Page Total, Page 1 of 9
Page Total, Page 2 of 9
Page Total, Page 3 of 9
Page Total, Page 4 of 9
Page Total, Page 5 of 9
Page Total, Page 6 of 9
Page Total, Page 7 of 9
Page Total, Page 8 of 9
Page Total, Page 9 of 9
Page Total, Page 10 of 12
Bill No. 3.1 Total Exclusive of VAT Carried to Section 3 Summary Sheet

## Chemical storage building
TETU-AGUTHI WATER SUPPLY PROJECT
BILL No. 3.2
CHEMICAL STORAGE AND MIXING BUILDING
ITEM | DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
No. |  |  |  | Kshs | Kshs.
1 | SUBSTRUCTURES (PROVISIONAL)
Excavations and Earthworks
The rates shall include for all strutting, shuttering,stabilising the excavation faces and keeping the excavation free of water by pumping, bailing or other means.
Bulk excavations and top soil stripping for all structures are measured under Bill No. 3.12 - Site and Ancillary Works.
Excavate below stripped level for foundations in common material, part backfill after construction and remainder, cart away to tips or use as fill on site, all as directed by the Engineer.
Excavate 0.00-1.50m deep starting from stripped level to receive :-
1.1 | Foundations | m3 | 170
Extra over excavation in any position for:-
1.2 | Excavating in compacted gravel or decomposed rock | m3 | 12
1.3 | Excavating in soft rock or hard material | m3 | 24
Approved selected Filling
1.4 | Fill and ram selected excavated materials around foundations and buildings | m3 | 64
Approved filling as described:-
1.5 | Provide and deposit approved imported murram in maximum 150mm thick layers in making up levels over 300mm thick including achieving satisfactory compaction | m3 | 33
1.6 | Provide and deposit approved hardcore fill material 300mm thick in making up levels including achieving satisfactory compaction | m2 | 72
1.7 | Provide, lay and level out, 50mm thick fine crushed stone, sand or gravel blinding to surface of filling, including watering and rolling to achieve satisfactory compaction | m2 | 72
Disposal of Surplus Spoil:-
1.8 | Cart away surplus excavated materials to an approved dumping site | m3 | 106
Anti-Termite Treatment
1.9 | Chemical anti-termite treatment to surface of filling with an approved insecticide | m2 | 122
Damp-proof Membrane
1.1 | 500 Gauge polythene sheeting, laid over hardcore in two layers | m2 | 244
PAGE TOTAL CARRIED TO BILL COLLECTION PAGE
Concrete Work:
Mass Concrete Class 15/20mm maximum aggregate as described in:-
1.11 | 75mm Thick blinding under foundation concrete | m2 | 10
Guaranteed Strength Reinforced Concrete Class 25/20mm maximum aggregate as described in:-
1.12 | Combined Footing and Columns | m3 | 26
1.13 | Strip Footing | m3 | 2
1.14 | Entrance Ramp | m3 | 1
1.15 | 150mm Thick Base Slab | m3 | 3
1.16 | 300mm Thick Base Slab | m3 | 18
1.17 | Extra over concrete for tamping whilst still green to make ribbed finish | m3 | 3
Guaranteed Strength Reinforced Concrete Class 25/20mm maximum aggregate as described in:-
1.18 | Isolated columns and piers in foundations | m3 | 2
Reinforcement
Fabric Reinforcement No. A142 Mesh Size 150 x 150mm Weighing 2.22 kgs Per m2 , Including Bends, Tying Wire and Distance Blocks:-
1.18 | Fabric reinforcement with minimum 150mm wide side and end laps, laid in bed | m2 | 66
Provide and Fix High Tensile Steel Reinforcement to SRN 127 including cutting, bending, propping with spacers and tying as specified :-
1.19 | Reinforcement, all diameters | Kg | 5000
Formwork
Provide and fix shuttering including propping, strutting and striking, all as specified
Sawn Formwork - Class F1 Finish:-
1.2 | Vertical sides of Combined Footings and columns in foundations | m2 | 50
Wrot Formwork - Class F3 Finish:-
1.21 | Edges of surface beds, plinths and Edges of the entrance Ramp (150mm high) | m | 13
Walling
Natural Stone Block Walling, Medium Chisel Dressed, Reinforced with 20 swg Hoop Iron at every alternate course, and Bedded, Jointed and Pointed in Cement Mortar (1:3):-
1.22 | 200 mm Walling | m2 | 43
PAGE TOTAL CARRIED TO BILL COLLECTION PAGE
Damp-proof course:
Bituminous felt damp-proof course as described:-
1.23 | 200mm Wide under walls | m | 34
SUPERSTRUCTURE
2 | CONCRETE, FORMWORK, REINFORCEMENT
Guaranteed Strength Reinforced Concrete Class 25/20mm as described in:
2.1 | 150mm Thick tank walls | m3 | 2
2.2 | 200mm Thick tank walls | m3 | 15
2.3 | Doser Platforms | m3 | 1
2.4 | 250mm Thick channel walls | m3 | 4
2.4 | Tank Base Slab and Doser Platforms | m3 | 5
2.5 | 200mm Thick solid suspended slab and First Floor Slab | m3 | 20
2.9 | 150mm Thick suspended ramp laid to slope not exceeding 15 degrees from horizontal | m3 | 4
2.1 | 250mm Thick solid suspended slab | m3 | 15
2.6 | External and Internal Stairs, Stair Landings and Stair Beams | m3 | 4
2.7 | Columns | m3 | 7
2.8 | Beams | m3 | 17
2.9 | Labour and material in forming lip in mixing tank concrete walls and partitions, lip 75mm wide x 150mm high with 75 x 75mm chamfered bottom edge. | m | 9
2.10 | Form scour and dosing pipework channel with 150mm thick RC walls internal size 300mm wide x 150mm deep in concrete floor slab including forming rebate 50mm wide x 50mm deep to top inner edges of channel wall to receive precast concrete cover slabs. | m | 19
Formwork
Provide and fix shuttering including propping, strutting and striking, all as specified
Sawn Formwork - Class F1 Finish :-
2.11 | Horizontal soffites of suspended slabs | m2 | 37
2.12 | Sloping soffites of ramp not exceeding 15 degrees from horizontal | m2 | 20
2.12 | Sloping soffites of External staircase and its Landings | m2 | 12
2.21 | Edges of slabs 250mm high | m | 6
2.13 | Risers of steps and Edge of Stairs | m2 | 8
2.23 | Raking open string edge of staircase 325mm (extreme) high including cutting bottom edge to profile of treads and risers | m | 2
Wrot Formwork - Class F3 Finish :-
2.14 | Edges of slabs 150mm high | m2 | 11
2.15 | Vertical sides of tank walls | m2 | 154
2.16 | Vertical sides of scour and dosing channel walls | m2 | 12
2.17 | Sloping soffites of Internal staircase and its Landings | m2 | 4
PAGE TOTAL CARRIED TO BILL COLLECTION PAGE
2.18 | Vertical sides of columns | m2 | 85
2.19 | Sides and soffites of beams | m2 | 149
2.2 | Horizontal Soffit of the First floor slab | m2 | 66
Reinforcement
Provide and Fix High Tensile Steel Reinforcement to SRN 127 including cutting, bending, propping with spacers and tying as specified :-
2.21 | Reinforcement, all diameters | Kg | 9600
Precast Reinforced Concrete (1:2:4) with minimum cube strength of 14 N/square millimetre at 7 days and 21 N/ square millimetre at 28 days as described in:
2.22 | Cover Slabs for Scour and Dosing channels | m2 | 6
2.23 | Precast concrete Pavement around the building | m2 | 48
3 | WALLING
External Walls
Selected Machine Dressed Natural Stone Block Walling, Reinforced with 20 swg Hoop Iron at every alternate courses, and Bedded, Jointed in Cement Mortar (1:3):-
3.1 | 200mm Thick walling | m2 | 110
Labours
3.2 | Extra over walling for ruled horizontal | m2 | 110
Precast Concrete Louvre Block Walling :-
3.3 | 200mm Thick louvre block walling with twin section with plastic coated coffee tray wire sandwiched between sections | m2 | 54
Dressed Stone Cills
3.4 | 200mm Thick x 275mm wide dressed stone cill bedded, jointed and pointed in cement mortar on top of 200mm wall | m | 28
Internal Walls
Solid Concrete Block Walling With Concrete Blocks to BS 2028, Type "A" with Minimum Crushing Strength of 3.7N/mm2 at 28 Days, Bedded, Jointed and Pointed in Cement Mortar (1:5):-
3.5 | 200mm Thick walling | m2 | 11
4 | ROOF COVERINGS
Concrete, single lap interlocking roof tiles on and including sawn cypress (Grade 2) battens size 40 x 40mm pressure impregnated with approved preservative:-
4.1 | Roof tiles | m2 | 111
PAGE TOTAL CARRIED TO BILL COLLECTION PAGE
Extra over roofing tiles for:-
4.2 | Ridge capping including bedding and pointing in cement sand (1:4) mortar with colouring to match colour of tiles. | m | 8
4.3 | Hip capping including bedding and pointing in cement sand (1:4) mortar with colouring to match colour of tiles. | m | 14
4.4 | Filled ends of ridge capping or hip capping | Nr | 6
4.5 | 500 Gauge polythene sheeting laid in two layers as underlay and nailed to rafters. | m2 | 111
4.6 | Fair raking cutting roofing tiles | m | 42
4.7 | Fair raking cutting corrugated sheet roofing | m | 42
5 | CARPENTRY AND JOINERY
Carpentry
Roof Timbers
Double Pitch Roof Truss in Sawn Cypress Grade II Seasoned and Pressure Impregnated with Wood Preservative and timber joints with bolted and nailed connections to the Engineer's approval :-
5.1 | Equal scissor truss 6000mm clear span and 1386 mm high with 6000 mm eaves projection, in 150 x 50mm rafters and ceiling joints/Rafter tie. | Nr | 4
5.2 | Equal Hip truss 5200 mm clear span and 1386 mm high with 600 mm eaves projection, in 150 x 50mm rafters and ceiling joints/Rafter tie. | Nr | 4
Other Roof Members
Sawn Cypress Grade II Maximum Moisture Content 12% Seasoned and Pressure Impregnated with Wood Preservative and timber joints with bolted and nailed connections to the Engineer's approval:-
5.3 | 100 x 50mm Intermediate rafters | m | 130
5.4 | 100 x 50mm Hip rafters | m | 21
5.5 | 150 x 50mm Purlins | m | 48
5.6 | 200 x 50mm Ridge board | m | 8
5.7 | 100 x 50mm Wall plate tied to wall with 20 s.w.g. hoop iron at 900mm centres | m | 37
5.8 | Scarfed joint to 200 x 50mm timber member | Nr | 1
5.9 | Scarfed joint to 150 x 50mm timber member | Nr | 4
Sundries
5.1 | Bed wall plate in cement mortar (1:3) | m | 37
PAGE TOTAL CARRIED TO BILL COLLECTION PAGE
Joinery
General Timbers
Wrot Prime Grade Cypress
5.11 | 250 x 40mm Fascia board | m | 43
6 | CEILING
12mm Thick Gypsum Board or approved Equivalenet Fixed to and including 50 x 50mm sawn cypress Grade 2 battens at 600mm centres in both directions complete with Gauge Jointing Material
6.1 | Ceiling laid to slope not exceeding 15 degrees fixed to underside of trusses | m2 | 94
6.2 | 12mm Cornice 50mm high laid to slope, plugged | m | 36
6.3 | Extra over ceiling lining for forming removable access trap door size 600 x 600mm with 100 x 38 mm sawn treated cypress trimming joists between tie beams,120 x 20mm (finished ) wrot cypress frame all round and 20mm blockboard removable panel set loose on top of framing. | Nr | 1
7 | METALWORK
Steel Doors
Pressed Metal Louvre Doors
Supply and Fix the following Pressed Metal Louvre Doors with 100 x 50mm Stiles and Top Rails, 150 x 50mm Middle and Bottom Rails With Pressed Metal Infill Louvres and 100 x 50mm Pressed Metal Frames, Including Hinges, Pad Bolts and Tower Bolts, All To Manufacturer's Details, with one coat lead oxide primer complete with opening accessories including bedding and pointing around frames in cement mortar:-
7.1 | Double door size 1800 x 2400 mm high in two equal panels | Nr | 2
7.3 | Double door size 1800 x 2500 mm high in two equal panels | nr | 1
uPVC Casement Windows
Supply and Fix the following Standard Section PVC Casement Windows, including 4mm Thick Clear Sheet Glass glazed to Steel Casements with Putty, Complete with Opening Accessories, Including Building in Lugs to Jambs and Head and Water-Proofing and Filling Around Opening with Approved Compound; and Including Burglar-Proofing Fabricated from 12 x 12mm Mild Steel Square Bars at 150mm Centres Vertically and 150mm Horizontally and Fixed Internally to Surrounding Wall with 12mm Mild Steel Fish-Tailed Lugs at Maximum 600mm Centres; all Finished with Three Coats Oil Paint, :-
7.2 | Window size 1797 x 597mm high with 1 No. fixed and 2 No. top hung opening bottom sashes and with permanent ventilator hood over (W5) | Nr | 8
PAGE TOTAL CARRIED TO BILL COLLECTION PAGE
7.3 | Window size 1797 x 1197mm high with 3 equal panels, with upper part having 2nr. fixed and 1nr. top-hung ventilator and lower half having 2nr. side hung panels opening outwards and 1nr. fixed panel (W1) | Nr | 4
7.4 | Window size 1597 x 1197mm high with 3 equal panels, with upper part having 2nr. fixed and 1nr. top-hung ventilator and lower half having 2nr. side hung panels opening outwards and 1nr. fixed panel (W2) | Nr | 3
Balustrades and Railings
Balustrade Unit 1000mm High comprising 40mm Diameter Galvanised Pipe Top, Middle and Bottom Rails and 40mm Diameter Galvanised Pipe Balusters Spaced at Maximum 1000mm centres and bottom end bent, fanged and built into mortice in concrete, including all necessary Welding:-
7.5 | Raking Balustrade unit 9000mm long, 6000mm and 3000mm | m | 9
7.6 | Level Balustrade unit 6000mm long, 4500mm and 1500mm | m | 6
RENDERING
12.5mm Thick Cement and Sand Render as described externally on :-
7.7 | Columns | m2 | 26
7.8 | Horizontal sides and soffites of beams | m2 | 149
8 | PLASTERING
12.5mm Thick Gauged Cement Plaster as Described Internally on :-
8.1 | Concrete or blockwork | m2 | 192
8.2 | Reveals of openings | m2 | 5
8.3 | Sloping soffites of ramp not exceeding 15 degrees from horizontal | m2 | 19
8.3 | Sloping soffites of staircase | m2 | 16
8.5 | Raking open string edge of staircase 295mm (extreme) high | m | 2
Screeds
Bonded cement and sand (1:4) screed bed in one coat, well bonded to concrete base as described:-
8.4 | 38mm Thick screed laid level to receive granito floor tiling | m2 | 128
8.5 | 12mm (minimum) Thick Cement and sand backing (1:4) with approved plasticiser to receive granito floor laid to skirtings, treads and risers (measured separately). | m2 | 20
Bonded cement and sand (1:4) screed bed in one coat with approved hardener incorporated in the mix, well bonded to concrete base as described:-
8.6 | 38mm Thick screed laid level to receive epoxy lining (measured separately) | m2 | 90
8.7 | 150 x 20mm Thick skirting with hardener laid with a square top edge and coved junction with floor finish | m | 130
PAGE TOTAL CARRIED TO BILL COLLECTION PAGE
Floor Tiling
Acid-proof Granito Floor Tiles :-
8.8 | Floor tiles laid on screed (measured separately) with straight joints both ways | m2 | 128
8.9 | Tiles laid to risers and treads of steps on screed (measured separately) with straight joints both ways | m2 | 20
8.1 | Tiles laid as skirting 150mm high | m | 130
8.11 | Provide and fix 12mm thick Acrilin Tank Wall Tiles fixed with tile adhesive with straight joints both ways | m2 | 37
Water Based Epoxy Floor and Wall Coating as 'MASTERTOP 1110T' applied strictly in accordance with the Manufacturer's printed instruction :-
8.12 | Coating laid to mixing tanks floors, walls and partitions | m2 | 90
8.13 | Coating laid to vertical skirting or upstand surfaces | m2 | 19.5
9 | PAINTING AND DECORATING
Prepare, knot, prime, stop and apply three coats first quality gloss paint to wood surfaces
Externally on:-
9.1 | General surfaces of fascia boards | m2 | 11
Prepare, touch up primer and apply three coats gloss paint :
Externally on:-
9.2 | General surfaces of louvred metal doors (measured flat overall) | m2 | 9
Internally on:-
9.3 | General surfaces of louvred metal doors (measured flat overall) | m2 | 9
Prepare and Apply Three Coats Exterior Quality Plastic Emulsion Paint:-
Externally on:-
9.4 | Fair-faced vertical concrete columns | m2 | 41
9.5 | Fair-faced horizontal sides and soffites of beams | m2 | 149
Prepare and Apply Three Coats Interior Quality Plastic Emulsion Paint:-
Internally on:-
9.6 | Plastered concrete or blockwork | m2 | 192
9.7 | Ditto reveals of openings | m2 | 5
10.8 | Ditto sloping soffites of ramp not exceeding 15 degrees from horizontal | m2 | 19
PAGE TOTAL CARRIED TO BILL COLLECTION PAGE
9.8 | Ditto sloping soffites of staircase exceeding 15 degrees from horizontal | m2 | 16
10.1 | Ditto raking open string edge of staircase 295mm (extreme) high | m | 2
9.9 | Horizontal soffites of suspended slabs | m2 | 85
Prepare and Apply Three Washable Distemper as Described to:-
9.1 | Sloping soffites of suspended plasterboard ceilings | m2 | 95
10.13 | Ditto 100-200mm girth | m | 60
10 | ALUM/SODA ASH MIXING TANKS
Note: All technical details including type, material, specification, etc. to be submitted with Tender for all chemical mixing equipment and pipework. Non-submission of above requirement will result in equipment to be supplied to approval of the Engineer and the cost quoted will deem to include the required approved materials and equipment.
10.1 | Provide and place 6mm stainless steel chemical dissolving tray | Nr | 5
Ranges for Soda Ash / Alum mixing tanks in Chemical Storage and Mixing Building
Supply all equipment to site, store, install, commission and maintain the following ranges and equipment, including all nuts, bolts, washers, packing etc.
10.2 | Five ranges complete of 25mm uPVC pipework for water supply to Soda Ash mixing tank and Alum mixing tanks including for making connection to domestic water supply main as per details. | Item | L.S
10.3 | Five ranges complete of 50mm diameter uPVC pipes and fittings for outlet from Soda Ash mixing tank and Alum mixing tanks to solution feed dosers as per details. | Item | L.S
10.4 | Five ranges complete of 80mm diameter uPVC pipes and fittings for overflow and for washout to Soda Ash mixing tank and Alum mixing tanks as per detaills. Include for all anchoring and supporting of all pipework and fittings. | Item | L.S
10.5 | Five ranges of pipework of 40mm diameter reinforced nylon pipe from chemical mixing tank to chemical dosing channel | Item | L.S
10.6 | 200mm dia. HDPE pipe to chemical dosing channel sleeve | m | 5.5
Provide and fix approved "Epofloor" lining in accordance with the manufacturer's instructions (supplied by Robbialac Paints or approved equivalent)
10.7 | 5mm lining to bottom of mixing tanks | m2 | 16
10.8 | 5mm lining to internal sides of mixing tanks | m2 | 54
PAGE TOTAL CARRIED TO BILL COLLECTION PAGE
10.9 | Provide and fix gravity solution feed dosers of capacity upto 50ml/s of Opados Type or approved equivalent complete with outlet funnels and flashes for Alum and Soda Dosing. | Nr | 5
10.10 | Provide and fix 300mm diameter exhaust extractor fan to be fixed in the chemical storage and mixing room. | Nr | 3
10.11 | Provide and fix electrically driven mixers for chemical mixing tanks. The shaft and impellers to be of non-corrosive material driven by electric motor (2.0 kw). Include for fixing on tanks. | Nr | 5
PAGE TOTAL CARRIED TO BILL COLLECTION PAGE
26.505
10.23

## Collection Sheet 3.2
TETU-AGUTHI WATER SUPPLY PROJECT
BILL No. 3.2
PAGE TOTALS COLLECTION SHEET
Amount
Kshs.
Page Total, Page 1 of 10
Page Total, Page 2 of 10
Page Total, Page 3 of 10
Page Total, Page 4 of 10
Page Total, Page 5 of 10
Page Total, Page 6 of 10
Page Total, Page 7 of 10
Page Total, Page 8 of 10
Page Total, Page 9 of 10
Page Total, Page 10 of 10
Bill No. 3.2 Total Exclusive of VAT Carried to Section 3 Summary Sheet

## Sedimentation Tanks
TETU-AGUTHI WATER SUPPLY PROJECT
BILL No. 3.3
SEDIMENTATION TANKS - 4 Nr
ITEM | DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
No. |  |  |  | (Kshs) | (Kshs)
1 | EXCAVATION
The rates shall include for all strutting, shuttering, stabilising the excavation faces, and keeping the excavation free of water by pumping, bailing or other means.
Bulk excavations and top soil stripping for all structures are measured under Bill No. 20 (Site & Ancillary Works).
Excavate below stripped level to formation level in common material, part backfill after construction and remainder, cart away to tips or use as fill on site, all as directed by the Engineer.
1.1 | Maximum depth n.e. 1.0 m | m3 | 450
1.2 | -Ditto- but maximum depth 1.0 m to 2.0 m | m3 | 837
1.3 | -Ditto- but maximum depth 2.0 m to 3.0 m | m3 | 217
1.4 | -Ditto- but maximum depth 3.0 m to 4.0 m | m3 | 18
1.5 | -Ditto- but for the scour chamber | m3 | 59
1.6 | Trimming surface for blinding layer of concrete sloping 30 (6%) to horizontal | m2 | 585
1.7 | -Ditto- 9o (16%) to horizontal | m2 | 234
1.8 | Excavate trench for 150 mm dia. pipes in common material, trimming sides and preparing trench bottoms, backfill with approved hardcore and compact after laying of pipework depth n.e. 1.2 m. Note: Sections under Sedimentation Tank base slab shall be backfilled with Class 20/20 mass concrete surround, measured under Concrete Works. | m | 66
1.9 | Transport approved excavated material from site and use as fill and compact in 200 mm layers as specified on site as and where directed by the Engineer. Compaction tests to be done and rates to include for this. | m3 | 20
1.1 | Extra over Items 1.1 to 1.3 for excavation in rock Class 'A', blasting not permitted (Provisional) | m3 | 96
1.11 | -Ditto- for excavation in rock Class 'B', blasting not permitted (Provisional) | m3 | 159
1.12 | -Ditto- for excavation in rock Class 'C', blasting not permitted (Provisional) | m3 | 64
PAGE TOTAL CARRIED TO SECTION COLLECTION SHEET
2 | CONCRETE WORKS
Provide, mix and place concrete as directed
2.1 | Plain concrete Class 15/20 in 75 mm blinding layer under base slab of sedimentation tanks | m3 | 46.8
2.2 | Plain concrete Class 15/20 in 75 mm blinding layer under base slab of sludge collection sumps | m3 | 1
2.3 | Plain concrete Class 15/20 in 75 mm blinding layer under base slab of scour chamber | m3 | 1
2.4 | Plain concrete Class 20/20 in surround to 150 mm dia. sludge removal pipes | m3 | 1
Vibrated, Reinforced concrete Class 25/20 in
2.5 | 400 mm Base Slab - Sedimentation tank | m3 | 131
2.6 | 300 mm Base Slab - Sloping Slab - 3o (6%) to horizontal | m3 | 88
2.7 | 300 mm Base Slab- Sloping Slab - 9⁰ (16%) to horizontal | m3 | 34
2.8 | 300 mm Base Slab - Sludge Collection Sumps | m3 | 3
2.9 | 300 mm Base Slab - Sludge Collection Channel | m3 | 11
2.1 | 200 mm Base Slab - Scour chamber | m3 | 2
2.11 | 200 mm Base Slab- Flocculated Water Channel | m3 | 9
2.12 | 200 mm Base Slab- Sedimentation Tank Inlet Channel | m3 | 5
2.13 | 200 mm Base slab - Walkways | m3 | 23
2.14 | 300 mm Walls - Sedimentation Tanks | m3 | 144
2.15 | 300 mm Walls - Sludge Collection Sumps | m3 | 3
2.16 | 300 mm Walls - Sludge Collection Channnel | m3 | 13
2.17 | 200 mm Walls - Scour chamber | m3 | 7
2.18 | 200 mm Walls - Flocculated Water Channel | m3 | 13
2.19 | 200 mm Walls - Sedimentation Tank Inlet Channel | m3 | 12
2.2 | Tie Beams | m3 | 22
2.21 | Cantilever platforms for Headstocks | m3 | 1
3 | REINFORCEMENT
Provide and fix high tensile steel reinforcement to SRN 127 including cutting, bending, propping with spacers and tying as specified
3.1 | Reinforcement, all diameters | Kg | 71280
PAGE TOTAL CARRIED TO SECTION COLLECTION SHEET
4 | FORMWORK
Provide and fix shuttering including propping, strutting and striking all as specified
(i) Vertical Formwork - Class F1 Finish
4.1 | Sides of 400 mm Base Slab - Sedimentation Tanks | m2 | 32
4.2 | Sides of 300 mm Base Slab - Sedimentation Tanks | m2 | 81
4.3 | Sides of 300 mm Base Slab - Sludge collection channel | m2 | 19
4.4 | Sides of 300 mm Base Slab - Sludge collection Sumps | m2 | 5
4.5 | Sides of 200 mm Base Slab - Scour chamber | m2 | 3
4.6 | Sides of 200 mm Base Slab - Flocculated Water Channel | m2 | 7
4.7 | Sides of 200 mm Base Slab - Inlet Water Channel | m2 | 6
4.8 | Sides of 200 mm Base Slab - Walkways | m2 | 104
4.9 | Sides of 200 mm Walls - Sump | m2 | 18
4.1 | Sides of 200 mm Walls - Sludge collection channel | m2 | 104
4.11 | Surfaces of walls, width 0.1 m kicker | m2 | 86
(i) Vertical Formwork - Class F2 Finish
4.12 | Sedimentation tank wall at expansion joints interface | m2 | 339
(iii) Vertical Formwork - Class F3 Finish
4.13 | Sides of Walls - Sedimentation Tank, width 0.3 m | m2 | 1753
4.14 | Sides of Walls - Scour chamber, width 0.2 m | m2 | 112
4.15 | Sides of Walls - Flocculated Water Channel, width 0.2 m | m2 | 118
4.16 | Sides of Walls -Inlet Water Channel, width 0.2 m | m2 | 110
4.17 | Sides of cantilever supports for headstock | m2 | 2
4.18 | Sides of tie beams depth n.e. 0.6m | m2 | 101
(iii) Horizontal Formwork - Class F3 Finish
4.19 | Soffit of Flocuculated Water Channel, width 1.3m | m2 | 39
4.2 | Soffit of Inlet Water Channel, width 0.8m | m2 | 23
4.21 | Soffit of Walkways, width 0.9m - 1.3 m | m2 | 121
4.22 | Soffit of tie beams, width 0.45 m | m2 | 38
(v) Sloping Formwork - Class F3 Finish
4.23 | Sloping side of cantilever support for headstock | m2 | 3
Other Formwork- Class F3 Finish
4.24 | Box out for 400mm x 400mm square inlet control penstock in concrete walls and making good after installation of penstocks | Nr | 8
4.25 | Form 200 mm dia. cylindrical openings, 200 mm high, in base slab of inlet channel of sedimentation tank | Nr | 60
4.26 | Box out for 400mm x 200mm collection trough in concrete walls and making good after installation of troughs | Nr | 12
PAGE TOTAL CARRIED TO SECTION COLLECTION SHEET
5 | PRECAST CONCRETE SLABS
Precast concrete Class 25/20 finished fair on all surfaces and reinforced as shown on drawings. Provide and fix:
5.1 | 75mm thick cover slabs size 1250mm long x 400mm wide including 2 Nr. mild steel key holes cast with slab for flocculated water channel | Nr | 75
6 | CONCRETE SURFACE FINISH
6.1 | Provide Class UF3 Finish for top of base slab of Sedimentation Tanks, Channels, Walkways, etc. | m2 | 409
6.2 | Provide all materials and finish surface of concrete with cement mortar 1:4 to required slope in sludge concentration pockets | m2 | 55
7 | CONSTRUCTION JOINTS
Provide and install the following waterstops in construction joints including all surface treatment, formwork, forming of rebate 20 mm x 20 mm and sealing of rebate with polysulphide sealant all as per Drawings and Specification.
7.1 | 200 mm wide expandite super-cast waterfoil PVC or similar approved waterstop in vertical/horizontal construction joints in walls | m | 400
7.2 | Approved expansion board, thickness 25mm between sedimentation tank 2 and Sedimentation tank 3 | m2 | 80
7.3 | Approved expansion board, thickness 25mm between sedimentation tank and settled water channel | m2 | 40
7.4 | Approved expansion board, thickness 25mm between sedimentation tank and flocculated water channel | m2 | 60
8 | METAL WORK
All steelwork to be completely cleaned by acid dipping prior to galvanising.
Galvanised mild steel tubular balustrades all framed and welded together, including all necessary labours and fittings on tubings:
8.1 | Provide and fix 900 mm high level balustrades of 40 mm diameter tubing Class B throughout, consisting of handrail and parallel middle rail 450 mm below the hand rail with balusters at maximum 1500 mm centres all | m | 210
8.2 | Provide and fix GMS settled water collection troughs length 3,300 mm made out of 6mm thick GMS sheet 4 Include 6 mm thick galvanised steel plate welded to end of trough | Nr | 12
8.3 | Provide and fix 254 mm x 146 mm x 31 kg/m GMS universal beams 6,600 mm long. Include for all materials, bolts, etc., drilling and fixing into concrete | Nr | 4
8.4 | Provide and fix GMS support clamps, including for all materials and necessary drilling and fixing to GMS universal beams or bracket as required | Nr | 24
8.5 | Provide and fix 100 mm x 100 mm x 8 kg/m angle bracket 700mm long fixed to beam by means of 2 Nr 12 mm rawl bolts 100 mm long4, include for all drilling | Nr | 12
8.6 | Provide and fix 750 mm x 450 mm x 6 mm thick M.S. Plate welded to collection trough and fixed to wall of Sedimentation Tank with 20 mm dia., 150 mm long rawl bolts. Include for packing and sealing of joint between plate and wall | Nr | 12
8.7 | Provide all materials and fix GMS CAT ladder, length 2.0m to inside of chamber | Nr | 2
8.8 | Provide all materials and fix GMS landing to scour chamber wall, 1000 mm x 1000 mm | Nr | 1
8.9 | Provide and fix lockable G.M.S Open Mesh Flooring to scour chamber 1600 mm x 1900 mm | Nr | 2
8.1 | Ditto but for- flocculated channel outlet 1250 mm x 2300 mm | Nr | 1
PAGE TOTAL CARRIED TO SECTION COLLECTION SHEET
9 | PAINTING AND DECORATING
Provide, prepare and apply one coat mordant solution, one undercoat and two coats gloss enamel paint on galvanised metal work externally on:
9.1 | Guardrail pipe and fittings including 900 mm high level balustrades | m | 210
9.2 | Decanting troughs | m2 | 60
9.3 | Exposed Pipework and fittings | Item | L.S
9.4 | Provide and apply 3 coats of approved epoxy paint on one coat epoxy primer to internal concrete surfaces of Sedimentation Tanks (water line only) ('Masterseal 180' as made by BASF or approved equivalent). | m2 | 900
10 | LEAK PROOF TESTING
10.1 | Allow for leakproof testing of all Sedimentation Tanks and flocculation water channel as specified | Item | L.S
11 | PIPEWORK, FITTINGS & VALVES
Supply Transport to Site and Store, install, test and commission including Jointing Material, Bolts Gaskets, Packing, Jointing Glues, etc. as Applicable
11.1 | 400mm x 400mm square opening penstock non-rising stem type with extended spindle & head stock (Ham baker or approved equivalent) | Nr | 8
Scour Pipework - Approved Lined Ferrous Pipes to Class NP16
11.2 | 150mm dia. single flanged 90° bend (Mark 1) | Nr | 4
11.3 | 150mm dia. all flanged gate valve with extension spindle and wheel Euro 20 Series, type 23 or approved equivalent (Mark B) | Nr | 4
11.4 | 150mm dia. flanged spigot pipe, length 1200mm with puddle flange at 380 mm from spigot end (Mark C) | Nr | 4
11.5 | 150mm dia. Coupling (Mark D) | Nr | 8
11.6 | 150 mm dia. plain ended pipe length 4m with couplings (Mark E1) | Nr | 1
11.7 | -Ditto- length 12m with couplings (Mark E2) | Nr | 1
11.8 | -Ditto- length 19m with couplings (Mark E3) | Nr | 1
11.9 | -Ditto - but length 27m with couplings (Mark E4) | Nr | 1
11.1 | 150mm dia. plain ended pipe, length 1200mm with puddle flange at 155mm from one end (Mark F) | Nr | 4
PAGE TOTAL CARRIED TO SECTION COLLECTION SHEET

## Collection Sheet 3.3
TETU-AGUTHI WATER SUPPLY PROJECT
BILL No. 3.3
PAGE TOTALS COLLECTION SHEET
Amount
Kshs.
Page Total, Page 1 of 5
Page Total, Page 2 of 5
Page Total, Page 3 of 5
Page Total, Page 4 of 5
Page Total, Page 5 of 6
Bill No. 3.3 Total Exclusive of VAT Carried to Section 3 Summary Sheet

## Filters
TETU-AGUTHI WATER SUPPLY PROJECT
BILL No. 3.4
FILTERS AND FILTER GALLERIES 8 Nr
ITEM | DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
No. |  |  |  | (Kshs) | (Kshs)
1 | EXCAVATION
The rates shall include for all strutting, shuttering, stabilising the excavation faces, and keeping the excavation free of water by pumping, bailing or other means.
Bulk excavations and top soil stripping for all structures are measured under Bill No. 20 (Site & Ancillary Works).
Excavate below stripped level to formation level in common material, part backfill after construction and remainder, cart away to tips or use as fill on site, all as directed by the Engineer.
1.1 | Maximum depth n.e. 1.0 m | m3 | 401
1.2 | Ditto but maximum depth 1.0 m to 2.0 m | m3 | 290
1.3 | Ditto but maximum depth 2.0 m to 3.0 m | m3 | 3
1.4 | Transport approved excavated materials from site and use as fill and compact in 200mm layers as specified on site as and where directed by the Engineer. |  | 30
1.5 | Provide approved hardcore and compact in layers of 200mm, blinded with final material 25mm thick | m3 | 122
1.6 | Extra over Items 1.1 to 1.3 for excavation in rock Class 'A', blasting not permitted (Provisional) | m3 | 42
1.7 | Ditto for excavation in rock Class 'B', blasting not permitted (Provisional) | m3 | 70
1.8 | Ditto for excavation in rock Class 'C', blasting not permitted (Provisional) | m3 | 28
PAGE TOTAL CARRIED TO SECTION COLLECTION SHEET
2 | CONCRETE WORKS
Provide, mix and place concrete as directed
Plain Concrete Class 15/20 in 75mm Blinding layer under
2.1 | Base slab for filters | m3 | 15
2.2 | Base slab for filter gallery | m3 | 7
2.3 | Base slab Back wash water channel | m3 | 4
2.4 | Mass Concrete Class 15/20 between filter water collection channel end wall and filter gallery wall | m3 | 13
Vibrated Reinforced Concrete class 25/20 in:
2.5 | Base slab filter | m3 | 55
2.6 | Base slab filter gallery | m3 | 27
2.7 | Wall settled water channel / filter | m3 | 40
2.8 | Wallsettled water channel/sedimentation tank | m3 | 11
2.9 | Wall filter / filter gallery | m3 | 40
2.1 | Side walls filter | m3 | 95
2.11 | Base slab settled water channel | m3 | 4
2.12 | Base slab filter inlet channel | m3 | 4
2.13 | Wall filter inlet channel | m3 | 12
2.14 | Cantilevered platforms for headstocks | m3 | 1
2.15 | Wall filter water collecting channel | m3 | 10
2.16 | Walls washwater overflow channel | m3 | 10
2.17 | Base washwater channel | m3 | 14
2.18 | Walls washwater collection trough | m3 | 7
2.19 | Base washwater collection trough | m3 | 8
2.2 | Wall filtered water channel | m3 | 12
2.21 | Top slab filtered water channel | m3 | 6
2.22 | External wall filter gallery | m3 | 6
2.23 | Walkway slabs | m3 | 2
2.24 | Ring Beams ground floor | m3 | 6
2.25 | External staircase (2 nr.) | m3 | 6
3 | REINFORCEMENT |  | 0
Provide high tensile steel reinforcement to SRN 127 including cutting, propping, spacing and tying as specified
3.1 | All diameters | Kg | 45120
PAGE TOTAL CARRIED TO SECTION COLLECTION SHEET
4 | FORMWORK
Provide and fix shuttering including propping, strutting and striking all as specified
Vertical Formwork Class F1 Finish
4.1 | 300 mm side for base slab filter | m | 76
4.2 | 300 mm side for base slab filter gallery | m | 106
Vertical Formwork Class F3 Finish
4.3 | 300 mm side for base slab filter collection channels | m | 95
4.4 | Wallsfilter collection channels (0.3m0.425m) | m | 95
4.5 | Wallsfilter collection channels (0.3m0.8) | m | 95
4.6 | WallsWash water channels (0.3m0.4m) | m | 32
Horizontal Formwork Class F2 Finish
4.7 | Soffit of slab inlet channel (0.6 m 0.8 m) | m2 | 26
4.8 | Soffit of walkway slab (0.1 m 0.3 m) | m2 | 13
4.9 | Soffit of slabsettled water channel (0.8m1.0m) | m2 | 32
Sloping Formwork F3 Finish
4.1 | Soffit of steps external staircase (1.0m 1.5m) | m2 | 14
Horizontal Formwork F3 Finish
4.11 | Soffit of landings external staircase (1.0 m 1.5 m) | m2 | 3
Vertical Formwork F2 Finish
4.12 | Sides of walls Filters/Filtered Water Channel, width 0.1 m | m | 231
4.13 | Ring beams (0.3 m 0.6m) | m2 | 34
Vertical Formwork F1 Finish
4.14 | External wallssettled water channel (1.0 m 2.0 m) | m2 | 94
Vertical Formwork F3 Finish
4.15 | Internal walls settled water channel (1.0 m2.0 m) | m2 | 77 | 0
Vertical Formwork F3 Finish
4.16 | Wall filter / filter gallery (4.5 m 6.0 m) | m2 | 310 | 0
Vertical Formwork F3 Finish
4.17 | Walls filter (3.4 m 4.8 m) | m2 | 967 | 0
4.18 | Wall inlet channel (1.0 m 1.5 m) | m2 | 90 | 0
4.19 | Walls filter collecting channel (0.5 m 1.0 m) | m2 | 126 | 0
4.2 | Walls filter gallery (1.5m1.8m) | m2 | 18 | 0
4.21 | 150 mm side walkways | m | 69
Sloping Formwork F3 Finish
4..22 | Cantilevered platforms for headstocks (0.1 m 0.3 m) | m | 2
Vertical Formwork F3 Finish
4.23 | Cantilevered platforms for headstocks (0.1 m 0.3 m) | m | 2
Horizontal Formwork F3 Finish
4.24 | Soffit of washwater collection trough (0.8 m 1.0 m) | m2 | 42
Vertical Formwork F3 Finish
4.25 | Walls washwater collection trough (0.4 m 0.8 m) | m2 | 85
4.26 | Walls filtered water channel (1.0 m 1.5 m) | m2 | 159
Horizontal Formwork F2 Finish
4.27 | Soffit of roof filtered water channel (1.0 m 1.5 m) | m2 | 39
PAGE TOTAL CARRIED TO SECTION COLLECTION SHEET
5 | CONSTRUCTION JOINTS
Provide and install the following waterstops in construction joints including all surface treatment, formwork, forming of rebate 20mm x 20mm and sealing of rebate with polysulphide sealant all as per Drawings and Specifications.
5.1 | 200 mm wide Expandite Supercast water foil PCV or similar approved waterstopin vertical /horizontal construction joints | m | 420
5.2 | Approved expansion board, thickness 25mm between sedimentation tank wall and settled water channel. | m2 | 51
5.3 | Ditto but between filter No. 4 and Filter No. 5 | m2 | 73
6 | OPENINGS
6.1 | Form 200 mm diameter opening through 150 mm base by placing G.I. Pipe sleeve and removing after concreting for filter inlet channel | Nr | 16
7 | PROVIDE CLASS UF3 FINISH
7.1 | Provide all materials and lay cement screed (1:4) to required falls as indicated (Avg. 50mm thick ) in washwater channel | m2 | 32
7.2 | Ditto in filtered water channel | m2 | 38
Provide all materials and lay grano finish on cement screed in:
7.3 | Filter gallery | m2 | 60
8 | FILTER UNDER DRAINAGE SYSTEM
Concrete Class 25/20 precast concrete:
8.1 | Provide all materials and fix with approved sealer, filter under drain slabs 1600 mm long (in 3 pieces) x 700 mm wide x 75 mm thick. Include for bolt holes and casting in 100 mm diameter pipe with puddle flange as detailed in the drawing. Include reinforcement and G.S. nipple as detailed. | Nr | 24
8.2 | Supply and fix 16 mm diameter G.S. bolts and nuts. | Nr | 112
8.3 | Ditto 100 mm diameter G.I. socketted tee with 12 mm diameter GMS nut welded on top and 12 mm diameter hole drilled. | Nr | 168
8.4 | Ditto 100 mm diameter uPVC Class 'E' pipe 1575 mm long lateral with 8 pairs of 10 mm diameter holes | Nr | 336
8.5 | Ditto 100 mm diameter uPVC end cap | Nr | 336
8.6 | Ditto 100 mm diameter uPVC faucet socket with G.I. male threaded on one end and PVC socket on the other end | Nr | 336
8.7 | Ditto 12 mm diameter brass nipple with anticlockwise and clockwise (B.S.F.) threads. | Nr | 168
Filter Media
8.8 | Provide gravel and form filters bed | m² | 130
8.9 | Provide sand and form filter sand bed | m² | 130
Support Brackets Provide and Fix:
8.1 | Mass Concrete Class 20/20 finished fair on all surfaces support blocks 220 mm x 100 mm x 180 mm for brackets for uPVC laterals with half round groove for resting laterals. Include fixing with mortar. Include for top GMS support plate & bolts as detailed. | Nr | 1008
PAGE TOTAL CARRIED TO SECTION COLLECTION SHEET
9 | METAL WORK
All steelwork to be completely cleaned by acid dipping prior to galvanising.
9.1 | Provide and fix 6 mm GMS deflector plate with 45o crank at 150 mm from one end fixed to concrete with 4 nr. 12 mm diameter rawl bolts. | Nr | 16
9.2 | Provide and fix C.I. Medium duty inspection cover size 600 mm x 450 mm with frames on filtered water channel | Nr | 4
9.3 | Provide and fix 900 mm high level balustrades of 40 mm diameter tubing Class 'B' throghout consisting of handrail and parallel middle rail 450mm below the handrail with balusters at maximum 1500 mm centres, all as detailed | m | 126
| Provide and fix balustrade unit 1000 mm high comprising 32 mm diameter galvanised pipe top,middle and bottom end bent, fanged and built into mortice in concrete. | m | 18
10 | MISCELLANEOUS
10.1 | Boxing out 1000 mm x 450 mm holes in Filter Gallery concrete wall for wash water Channel exit to wash water Chamber and making good after construction of the Channel. | Nr | 1
10.2 | Ditto but 600 mm x 550 mm holes on filter/overflow wash water reinforced concrete wall for wash water trough. | Nr | 8
10.3 | Ditto but 450 mm x 250 mm holes | Nr | 12
10.4 | Ditto but 250 mm x 250 mm holes in settled/filter inlet channel wall for inlet penstock | Nr | 8
10.5 | Boxing out 350 mm dia. holes in the side walls of the filter gallery for wash water inlet pipe and making good after pipe laid | Nr | 1
10.6 | Ditto but 300 mm dia. holes for filtered water pipes and backwash water pipes | Nr | 24
10.7 | Ditto but 200mm dia. holes in filtered water channel for filtered water outlet pipes | Nr | 8
10.8 | Ditto but 450mm dia. Holes in filtered water channel wall for filtered water ountlet to the tank | Nr | 1
10.9 | Ditto but 100mm dia. holes through the slab of control room for Valve stems | Nr | 32
10.1 | Ditto but for 1000mm dia holes for Air Wash Pipe | Nr | 9
10.11 | Ditto but 600 mm x 450 mm holes for inspection chambers on the roof slab of filteres water channel | Nr | 4
10.12 | Allow for cutting, grouting and making good any holes, chases etc. for all fittings and pipework fixing and electrical work in the filters, filter gallery and filter control room | Item | L.S
10.13 | Provide all materials and fix to concrete air pipe supports, include for 3 coats of paint | Nr | 8
10.14 | Allow for leak proof testing of all the filters as specified | Item | L.S
10.15 | Provide, prepare and apply one coat mordant solution, one undercoat and two coats gloss enamel paint on galvanised metalwork externally on handrail pipe and fittings in 900 mm high level balustrade. | m | 126
10.16 | Dittobut for a 1000mm high raking balustrade | m | 18
10.17 | Provide concrete support for washwater outlet and overflow measuring 775mm x 400mm x 300mm high with bituminous felt padding and 80mm x 6mm hick flat flat Gms plate anchored to the support by 2 nr. 6mm diameter bolts. | Nr | 8
10.18 | Provide mass concrete class 15/20 thrust blocks under 200mm dia. gate valves. | Nr | 8
10.19 | Ditto but for 300mm dia. gate valve. | Nr | 8
10.2 | Ditto but under 200mm dia. gate valves. | Nr | 8
10.21 | Allow for painting of all filtered water pipework to approved standards with 3 coats of super gloss paint applied on one coat primer. Colour selection to be approved by the Engineer. | Item | L.S
10.22 | Ditto but for washwater inlet and washwater outlet pipework | Item | L.S
10.23 | Ditto but for AIR WASH pipework. | Item | L.S
10.24 | Ditto but for overflow pipework. | Item | L.S
10.25 | Provide & fix over settled water channel precast concrete walkway slabs 950mm x 400mm x 75mm thick with 2No. mild steel key holes. | Nr | 74
10.26 | Provide all materials (including tile adhesive, etc) and fix white ceramic tiles in filtered water channel. | m² | 107
10.27 | Provide and apply Epoxy wall and floor coating, 'MASTERTOP 1110T' or approved equivalent, on internal surfaces of filter walls and floor. | m² | 724
PAGE TOTAL CARRIED TO SECTION COLLECTION SHEET
11 | PIPEWORK, FITTINGS & VALVES
Supply, transport to site and store, install, test and commission.
Filter Inlet
11.1 | 250 mm C.I. square Inlet Control penstock nonrising stem type complete with extension spindle and headstock with handwheel HamBaker or approved equivalent. | Nr | 8
Air Main Pipework Approved lined ferrous pipes
11.2 | 100mm dia. flanged spigot pipe 4105mm long with spigot end blanked off and 21Nr. 12mm dia. holes and hexagon nuts welded at 215mm and 310mm c/c on underside as per details (Mark a) | Nr | 8
11.3 | 100mm dia. all flanged special tee with 2Nr. 12mm dia. holes and hexagon nuts welded at 215mm c/c on underside (Mark b) | Nr | 8
11.4 | 100mm dia. flanged spigot pipe 205mm long with spigot end blanked off and 1Nr. 12mm dia. hole and hexagon nut welded at 90mm from spigot end as per details (Mark c) | Nr | 8
11.5 | 100 mm dia. all flanged pipe, 2950 mm long (Mark d) | Nr | 8
11.6 | 100 mm dia. all flanged 90o bend (Mark e) | Nr | 10
11.7 | 100 mm dia. flanged spigot pipe, 1757 mm long (Mark f) | Nr | 8
11.8 | 100 mm dia. flange adaptor (Mark g) | Nr | 8
11.9 | 100 mm dia. all flanged gate valve with extended nonrising spindle length 410mm and headstock with handwheel to SRN 501 (Mark h) | Nr | 8
11.1 | 100mm x 100mm dia. all flanged tee (Mark i) | Nr | 8
11.11 | 100mm dia. all flanged pipe, 3160mm long (Mark j) | Nr | 7
11.12 | 100mm dia. blank flange (Mark k) | Nr | 1
11.13 | 100mm dia. all flanged pipe, 2685mm long (Mark l) | Nr | 1
11.14 | 100mm dia. flanged spigot pipe 4000mm long (cut to suit on site) (Mark m) | Nr | 1
11.15 | 100mm dia. flange adaptor (Mark n) | Nr | 1
11.16 | 100mm dia. flanged spigot pipe 1200mm long (Mark o) | Nr | 1
11.17 | 100mm dia. Flanged nonreturn valve (Mark p) | Nr | 1
11.18 | 150mm x 100mm flanged concentirc taper (Mark q) | Nr | 1
11.19 | 150mm dia. flanged spigot pipe 1200mm long (Mark r) | Nr | 1
Filtered Water Outlet Pipework Approved Lined Ferrous Pipes
11.2 | 300mm dia. special flanged bellmouth 500mm long with puddle flange at 100mm from bellmouth end (Mark 1) | Nr | 8
11.21 | 300mm dia. all flanged pipe, 1520mm long with puddle flange at 500mm from one end (Mark 2) | Nr | 8
11.22 | Special all flanged cross 300mm x 300mm x 300mm x 300mm (Mark 3) | Nr | 8
11.23 | 300mm x 200mm dia. all flanged concentric taper (Mark 4) | Nr | 16
11.24 | 200mm dia. alll flanged gate valve with extension spindle, length 4.8m and headstock with handwheel to SRN 501 (Mark 5) | Nr | 8
11.25 | 200mm dia. flanged spigot 900 `bend (Mark 6) | Nr | 8
11.26 | 200mm dia. all flanged gate valve, with extension spindle, length 4.8m and headstock with handwheel to SRN 501 (Mark 7) | Nr | 8
11.27 | 200mm dia. flange adaptor (Mark 8) | Nr | 8
11.28 | 200mm dia. plain ended pipe 475mm long with puddle flange at 75mm from one end (Mark 9) | Nr | 8
PAGE TOTAL CARRIED TO SECTION COLLECTION SHEET
Washwater Inlet Approved Lined Ferrous Pipes
11.29 | 300mm dia. all flanged gate valve with extension spindle, length 4.8m and headstock with handwheel to SRN 501 (Mark 10) | Nr | 8
11.3 | 300mm dia. all flanged 900 short radius special bend (Mark 11) | Nr | 16
11.31 | 300mm dia. all flanged pipe 2000mm long (Mark 12) | Nr | 8
11.32 | 350mm x 350mm x 300mm dia. all flanged tee (Mark 13) | Nr | 8
11.33 | 350mm dia. blank flange (Mark 14) | Nr | 1
11.34 | 350mm dia. all flanged pipe 2850mm long (Mark 15) | Nr | 7
11.35 | 350mm dia. all flanged pipe 3950mm long (Mark 16) | Nr | 1
11.36 | 350mm dia. all flanged 900 short radius bend (Mark 17) | Nr | 2
11.37 | 350mm dia. flanged spigot pipe 2000mm long (Length cut to suit on site) (Mark 17A) | Nr | 1
11.38 | 350mm dia. flange adaptor (Mark 17B) | Nr | 1
11.39 | 350mm dia. flanged spigot pipe 1200mm long (Mark 17C) | Nr | 1
11.4 | 350mm dia. coupling (Mark 17D) | Nr | 1
Washwater Outlet Approved Lined Ferrous Pipes
11.41 | 300mm dia. flanged spigot pipe 525mm long with puddle flange at 150mm from spigot end (Mark 18) | Nr | 8
11.42 | 300mm dia. all flanged 900 short radius special bend (Mark 19) | Nr | 8
11.43 | 300mm dia. all flanged gate valve with extended nonrising spindle, length 4.0m and nonrising type headstock with handwheel to SRN 501 (Mark 20) | Nr | 8
11.44 | 300mm dia. special flanged spigot 900 short radius bend (Mark 21) | Nr | 8
Overflow Pipework Approved Lined Ferrous Pipes
11.45 | 200mm dia. flanged spigot pipe 470mm long with puddle flange at 150mm from spigot end (Mark 22) | Nr | 8
11.46 | 200mm dia. all flanged 900 bend (Mark 23) | Nr | 8
11.47 | 200mm dia. flanged spigot pipe, 3675mm long (Mark 24) | Nr | 8
Filtered Water Outlet to Treated Water Tank Pipework
11.48 | 450mm dia flanged spigot pipe 470mm long with puddle flange at 150 mm from the spigot end;600mm long (mark 25) | Nr | 1
11.49 | 450mm dia coupling (Mark 26) | Nr | 1
12 | BUILDING WORKS FILTER CONTROL ROOM, EXTERNAL STAIRCASE & FILTER GALLERY REAR AND SIDE WALLS
12.1 | CONCRETE
Guaranteed Strength Reinforced Concrete Class 25/20mm as Described in:
12.1.1 | Columns, beams and stairs | m3 | 17
12.1.2 | 150mm Thick solid suspended floor and landing slabs | m2 | 164
12.2 | FORM WORK
Provide and Fix Shuttering Including Propping, Strutting and Striking, all as Specified
Sawn Formwork Class F1 Finish :
12.2.1 | Horizontal soffites of suspended floor and landing slabs 4.50 6.00m high | m2 | 164
12.2.2 | Sides and soffites of downstand staircase beams | m2 | 3
12.2.3 | Edges of slabs, ramps and risers of steps not exceeding 300mm wide | m | 24
12.2.4 | Raking open string edge of staircase not exceeding 325mm (extreme) high including cutting bottom edge to profile of treads and risers | m | 13
Wrot Formwork Class F3 Finish :
12.2.5 | Sides and soffites of beams | m2 | 144
PAGE TOTAL CARRIED TO SECTION COLLECTION SHEET
12.3 | REINFORCEMENT
Provide and Fix High Tensile Steel Reinforcement to SRN 127 including Cutting, Bending, Propping With Spacers and Tying as Specified :
12.3.1 | Reinforcement, all diameters | Kg | 5054 | 0
12.4 | WALLING
External Walls
Selected Machine Dressed Natural Stone Block Walling, Reinforced with 20 swg Hoop Iron at every third courses, and Bedded, Jointed and Pointed in Cement Mortar (1:5):
12.4.1 | 200mm Thick walling | m2 | 200 | 0
Labours
12.4.2 | Extra over walling for ruled horizontal and flush vertical joints | m2 | 200 | 0
Precast Concrete Cills
12.4.3 | 200mm Thick x 275mm wide precast concrete cill bedded, jointed and pointed in cement mortar on top of 200mm wall. | m | 43
12.5 | CARPENTRY AND JOINERY
Carpentry
Roof Trusses
Double Pitch Roof Truss With 600mm eaves projection, in 150 x 50mm Rafters, Ceiling Joists, Struts and Ties in Sawn Cypress Grade II Seasoned and Pressure Impregnated with Wood Preservative and Timber Joints With Bolted and Nailed Connections to the Engineer's Approval :
12.5.1 | Equal truss 4375mm clear span and 906mm high | Nr | 6
Other Roof Members
Sawn Cypress Grade II Maximum Moisture Content 12% Seasoned and Pressure Impregnated with Wood Preservative and timber joints with bolted and nailed connections to the Engineer's Approval:
12.5.2 | 150 x 50mm Intermediate, hip and valley rafters | m | 165
12.5.3 | 150 x 75mm Purlins | m | 170
12.5.4 | 180 x 50mm Ridge board | m | 26
12.5.5 | 100 x 50mm Wall plate tied to wall with 20 s.w.g. hoop iron at 900mm centres and bedded in cement mortar (1:4) on top of wall | m | 70
Joinery
General Timbers
Wrot Prime Grade Cypress, Including Finishing With Three Coats First Quality Gloss Paint :
12.5.6 | 250 x 40mm Fascia board fixed with screws | m | 75
12.5.7 | Tongue & Groove (T&G) Boarding on underside of roof overhang, including provision of roof venting holes with gauze. | m2 | 46
12.6 | ROOF COVERINGS
Concrete, Single Lap Interlocking Roof Tiles on and including Sawn Cypress (Grade 2) Battens Size 40 x 40mm Pressure Impregnated with Approved Preservative:
12.6.1 | Roof tiles | m2 | 203
Extra over roofing tiles for:
12.6.2 | Ridge capping including bedding and pointing in cement sand (1:4) mortar with colouring to match colour of tiles | m | 26
12.6.3 | Hip capping ditto | m | 15
12.6.4 | Filled ends of ridge capping or hip capping | Nr | 4
12.6.5 | Gauge 28 galvanised corrugated sheets laid as laid as underlay and nailed to rafters | m2 | 203
12.6.6 | Fair raking cutting roofing tiles | m | 74
12.6.7 | Fair raking cutting corrugated sheet roofing | m | 74
PAGE TOTAL CARRIED TO SECTION COLLECTION SHEET
12.7 | METALWORK
Steel Doors
Pressed Metal Louvre Doors
Supply and Fix the following Pressed Metal Louvre Doors with 100 x 50mm Stiles and Top Rails, 150 x 50mm Middle and Bottom Rails With Pressed Metal Infill Louvres and 100 x 50mm Pressed Metal Frames, Including Hinges, Pad Bolts and Tower Bolts, All To Manufacturer's Details, with three coats gloss paint complete with opening accessories including bedding and pointing around frames in cement mortar:
12.7.1 | Double door size 1200 x 2400 mm high in two equal panels (D2a) | Nr | 2
Steel Casement Doors
Supply and Fix the following Standard Section Steel Casement Doors Including Hinges, Pad Bolts and Tower Bolts, All To Manufacturer's Details, including 4mm Thick Clear Sheet Glass And Glazing to Steel Casements with putty, three coats gloss paint, complete with opening accessories and bedding and pointing around frames in cement mortar:
12.7.2 | Double door size 1200 x 2400 mm high in two equal panels (D3) | Nr | 2
Steel Casement Windows
Supply and Fix the following Standard Section PVC Casement Windows, including 4mm Thick Clear Sheet Glass glazed to Steel Casements with Putty, Complete with Opening Accessories, Including Building in Lugs to Jambs and Head and WaterProofing and Filling Around Opening with Approved Compound; and Including BurglarProofing Fabricated from 12 x 12mm Mild Steel Square Bars at 150mm Centres Vertically and 150mm Horizontally and Fixed Internally to Surrounding Wall with 12mm Mild Steel FishTailed Lugs at Maximum 600mm Centres; all Finished with Three Coats Oil Paint, :
12.7.3 | Window size 1800 x 1200mm high with 2 No. fixed and 1 No. tophung opening bottom sashes and with permanent ventilator hood over (W1) | Nr | 24
12.8 | CEILING
12mm Thick Approved Plasterboard in Sheets Size 2400 x 1200mm Fixed to and Including 50 x 50mm Sawn Cypress Grade 2 Battens at 600mm Centres in Both Directions Complete with Gauge Jointing Material
12.8.1 | Horizontal ceiling fixed to underside of trusses | m2 | 127
12.8.2 | 12mm Cornice 50mm high, plugged | m | 69
12.8.3 | Extra over ceiling lining for forming removable access trap door size 600 x 600mm with 100 x 38 mm sawn treated cypress trimming joists between tie beams,120 x 20mm (finished ) wrot cypress frame all round and 20mm blockboard removable panel set loose on top of framing. | Nr | 1
Builders Work in Connection with Electrical Installations
12.8.4 | Allow for cutting and leaving all necessary holes, notches, mortices, sinkings and chases both in the structure and its finishes and for all making good in connection with concealed conduits or cables. | Item | L.S
PAGE TOTAL CARRIED TO SECTION COLLECTION SHEET
12.9 | RENDERING
12.5mm Thick Cement and Sand Render as Described Externally on :
12.9.1 | Blockwork and concrete surfaces | m2 | 124
12.1 | PLASTERING
12.5mm Thick Gauged Cement Plaster as Described Internally on :
12.10.1 | Blockwork and concrete surfaces | m2 | 200
12.10.2 | Sloping concrete surfaces | m2 | 3
12.11 | SCREED AND BACKING
Bonded Cement and Sand (1:4) Screed Bed or Backing in One Coat, Well Bonded to Concrete or Blockwork base as Described:
12.11.1 | 13mm Thick backing with approved plasticiser to receive wall tiles or floor tiles laid as skirting (measured separately) | m2 | 16
12.11.2 | 38mm Thick screed laid level to receive porcelain or ceramic floor tiling (measured separately) | m2 | 177
12.12 | FLOOR TILING
Ceramic Floor Tiles Laid With Straight Joints Both Ways:
12.12.1 | Floor tiles laid to floors, treads, risers or as skirting on screed or backing (measured separately) | m2 | 177
12.12.2 | Tiles laid level or on rake as skirting 150mm high | m | 100
12.13 | Precast Concrete Paving Slabs
12.13.1 | Slabs size 600 x 600 x 50mm Thick laid on and including 50mm thick bed of sand and jointing and pointing in cement mortar. | m2 | 49
12.14 | PAINTING AND DECORATING
Prepare and Apply Three Coats Exterior Quality Plastic Emulsion Paint:
Externally on:
| Fairfaced concrete surfaces | m2 | 124
Prepare and Apply Three Coats Interior Quality Plastic Emulsion Paint:
Internally on:
12.14.1 | Plastered blockwork and concrete surfaces | m2 | 200
12.14.2 | Plastered sloping concrete surfaces | m2 | 3
Prepare and Apply Three Coats Washable Distemper as Described to:
12.14.3 | Horizontal soffites of suspended chipboard or plasterboard ceilings | m2 | 127
PAGE TOTAL CARRIED TO SECTION COLLECTION SHEET
13 | Miscellaneous
13.1 | Provide and apply approved industrial epoxy floor paint on filter Gallery floor | m2 | 60
13.2 | Provide and apply 3 coats of approved grey epoxy paint on concrete wall in filter gallery after making good boxouts for pipework | m2 | 176
13.3 | provide and install fire hose reels with 20m long hoose pipe, to be fixed on filter gallery wall. Include for all plimbing , isolating pipework and connecting on site water supply system | Nr. | 2
14 | MISCELLANEOUS
14.1 | Provide and apply approved industrial Epoxy floor paint on the Filter Gallery Floor | m2 | 130
13.2 | Provide and apply 3 coats of approved Grey Epoxy paint on concrete wall in Filter Gallery after making good boxouts for Pipework | m2 | 176
13.3 | Provide and install fire hose reels with 20m long hose pipe, to be fixed on Filter Gallery wall. Include for all plumbing, isolating pipework and connecting to Onsite water supply system | Nr | 2
PAGE TOTAL CARRIED TO SECTION COLLECTION SHEET

## Collection Sheet 3.4
TETU-AGUTHI WATER SUPPLY PROJECT
BILL No. 3.3
PAGE TOTALS COLLECTION SHEET
Amount
Kshs.
Page Total, Page 1 of 11
Page Total, Page 2 of 11
Page Total, Page 3 of 11
Page Total, Page 4 of 11
Page Total, Page 5 of 11
Page Total, Page 6 of 11
Page Total, Page 7 of 11
Page Total, Page 8 of 11
Page Total, Page 9 of 11
Page Total, Page 10 of 11
Page Total, Page 11 of 11
Bill No. 3.4 Total Exclusive of VAT Carried to Section 3 Summary Sheet

## Treated Water Tank
TETU-AGUTHI WATER SUPPLY PROJECT
BILL No. 3.5
TREATED WATER TANK (500m³ CAPACITY)
ITEM | DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
No. |  |  |  | (Kshs) | (Kshs)
1 | GENERAL ITEMS
1.1 | Allow for testing, cleaning and sterilisation of Reservoir in accordance with specifications. | Item | L.S
1.2 | Allow for pressure testing, cleaning and sterilisation of Pipework in accordance with specifications | Item | L.S
2 | EARTHWORKS
The rates shall include for all strutting, shuttering, stabilising the excavation faces, and keeping the excavation free of water by pumping, bailing or other means
Bulk excavations and top soil stripping for all structures are measured under Bill No. 3.11 (Site & Ancillary Works).
Excavate below stripped level to formation level in common material, part backfill after construction and remainder, cart away to tips or use as fill on site, all as directed by the Engineer.
2.1 | Maximum depth n.e. 1.0 m | m3 | 253
2.2 | -Ditto- but maximum depth 1.0 m to 2.0 m | m3 | 253
2.3 | -Ditto- but maximum depth 2.0 m to 3.0 m | m3 | 253
2.4 | -Ditto- but maximum depth 3.0 m to 4.0 m | m3 | 164
2.6 | Transport approved excavated material from site and use as fill and compact in 200 mm layers as specified on site as and where directed by the Engineer. Compaction tests to be done and rates to include for this | m3 | 541
2.7 | Provide approved hardcore material and compact in layers of 200 mm, blinded with final material 75 mm thick | m3 | 70
2.8 | Extra over Items 2.1 to 2.5 for excavation in rock Class 'A', blasting not permitted (Provisional) | m3 | 57
2.9 | -Ditto- for excavation in rock Class 'B', blasting not permitted (Provisional) | m3 | 95
2.1 | -Ditto- for excavation in rock Class 'C', blasting not permitted (Provisional) | m3 | 38
3 | IN SITU CONCRETE
Provision of Concrete
Provide materials and mix concrete to the specified class; cement to BS 12
3.1 | Designed mix; Grade C15; 20mm aggregate | m3 | 30
PAGE TOTAL CARRIED TO BILL COLLECTION PAGE
3.2 | Designed mix; Grade C25; 20mm aggregate | m3 | 275
Placing of Concrete
Place, vibrate and cure concrete in the following elements of the structure as per details on drawings
Mass Concrete; Class 15/20
3.3 | Blinding under base slab; thickness 75mm | m3 | 12
Reinforced Concrete; Class 25/20
Bases, Footings, Pipe Caps, and Ground Slabs; >150 Thickness <300mm
3.4 | External wall base including key and splay | m3 | 68
3.5 | Base slab laid to slopes | m3 | 34
3.6 | Bases to columns | m3 | 1
3.7 | Bases to internal baffle walls | m3 | 1
3.8 | Base to overflow chamber | m3 | 1
Suspended Slabs; Thickness >150 <300mm
3.9 | Top slab including all upstands | m3 | 43
Walls; Thickness >150 <300mm
3.1 | Main external walls, 300mm thick | m3 | 51
3.11 | Baffle walls | m3 | 4
3.12 | Walls - washout sump | m3 | 1
3.13 | Walls - overflow chamber | m3 | 2
Walls; Thickness >300 <500mm
3.14 | Main external walls, 500mm thick | m3 | 60
Columns; Cross-Sectional Area >0.03 <0.1m²
3.15 | Columns excluding top flared heads | m3 | 1
Other Concrete Forms
3.16 | Top flared heads of columns | m3 | 1
4 | CONCRETE ANCILLARIES
Dimensions as per details on Specific Structural Drawings
Formwork: Rough Finish; Plane Vertical
4.1 | External sides of base slab; width >0.2 <0.4m | m2 | 13
4.2 | Both sides of key; width >0.4 <1.22m | m2 | 96
4.3 | External sides of washout sumps: width exceeding 1.22m | m2 | 5
PAGE TOTAL CARRIED TO BILL COLLECTION PAGE
Formwork: Fair Finish; Plane Horizontal
4.4 | Soffit of overflow chambers; width >0.4 <1.22m | m2 | 2
4.5 | Soffit of suspended slab; width exceeding 1.22m | m2 | 152
Formwork: Fair Finish; Plane Sloping
(Provisional Items - Only if no-recoverable formwork is required)
4.6 | Splay in wall; width >0.2 <0.4m | m2 | 14
4.7 | Splay out base slab; width >0.2 <0.4m | m2 | 84
4.8 | Splay at column heads; width >0.4 <1.22m | m2 | 3
Formwork: Fair Finish; Plane Vertical
4.9 | Internal sides of washout sumps; width >0.4 <1.22m | m2 | 3
4.1 | Inner sides of access manholes; width >0.4 <1.22m | m2 | 3
4.11 | Both sides of overflow chamber; width exceeding 1.22m | m2 | 16
4.12 | Outer side of access manholes upstands 300mm high; width exceeding 2m | m2 | 2
4.13 | Inner side of roof upstands 300mm high; width exceeding 2m | m2 | 15
4.14 | Outer side of roof upstands 550mm high; width exceeding 2m | m2 | 28
Walls
4.15 | External side | m2 | 286
4.16 | Internal side; wall thickness 500mm | m2 | 91
4.17 | Internal side; wall thickness 300mm | m2 | 160
4.18 | Both sides of baffle walls | m2 | 49
Formwork: Fair Finish; For Voids
4.19 | Large void 1400mm x 1370mm deep for overflow chamber | m2 | 2
Formwork: Fair Finish; Concrete Components of Constant Cross-section
Columns
4.2 | Sides of columns; 300mm x 300mm - 2 No. columns | m2 | 7
Other Members
4.21 | Sides of column bases; 1000mm x 1000mm - 2 No. bases | m2 | 2
4.22 | 50mm x 50mm rebates for access manhole cover | m | 5
4.23 | Ditto but for overflow chamber cover | m | 5
4.24 | 12mm dia. half round fillet for drip mould round soffit of roof slab overhang | m | 51
PAGE TOTAL CARRIED TO BILL COLLECTION PAGE
4.25 | Fillet to form 25mm x 25mm chamfer for all roof slab upstands & manhole upstands | m | 111
4.26 | Boxing out 550mm x 550mm holes in concrete wall of tank for inlet pipe | Nr | 1
4.27 | Boxing out 250mm dia. hole in concrete wall of sump in tank & making good after installation of pipework | Nr | 1
4.28 | -Ditto - but size 400mm dia. hole in base of overflow chamber | Nr | 1
4.29 | -Ditto - but size 1020mm x 1020mm hole in roof slab of tank | Nr | 1
Reinforcement; Deformed High Yield Steel Bars to BS4449
Rate to include for cutting, bending, supporting, trying and securing reinforcement
4.3 | Reinforcement, all diameters | t | 33
4.31 | Steel fabric to BS4483: A252 square mesh; nominal mass 3 - 4 kg/m² | m2 | 160
Construction Joints
Provide and install the following waterstops in construction joints including all surface treatment, formwork, forming of rebate and sealing of rebate with polysuphide sealant, all as per drawings and specification
4.32 | Open/Formed surface with filler; average width n.e. 0.5m | m2 | 22
4.33 | Plastic horizontal waterstops; rear guard type, width 200mm | m | 47
4.34 | Plastic vertical waterstops, width 200mm | m | 106
4.35 | Sealed 20mm x 20mm rebates with polysuphide joint sealant | m | 22
4.36 | 80mm Dia Ferrous Roof Drain Pipe (cut to suit on site) | m | 5
Miscellaneous Work (including provision and laying)
4.37 | 500 gauge polythene sheeting on blinding below base slab | m2 | 235
4.38 | Average 100mm thick layer of pumice on roof slab | m2 | 152
5 | PIPEWORK - FITTINGS AND VALVES
Rate to include for Supply, Transport to Site, Store, Install, Test & Commission. Include for Excavation & Backfilling of Pipe Trenches Where Applicable. Include Jointing Material, Bolts, Gaskets, Packing, Jointing Glues, etc., As Applicable
All Diameters are Nominal
Approved Lined Ferrous Pipes Fittings to NP 16
Distribution Outlet Ferrous Pipes Fittings & Valves
5.1 | 400mm dia. Special Flanged Bellmouth, 415mm length, with Puddle Flange 170mm from the Bellmouth End (Mark A) | Nr | 1
PAGE TOTAL CARRIED TO BILL COLLECTION PAGE
5.2 | 400mm dia. 90° Double Flanged Short Radius Bends (Mark B) | Nr | 2
5.3 | 400mm dia. Double Flanged Pipe, length 5500mm with Puddle Flange 5050mm from one end (Mark C) | Nr | 1
5.4 | 400mm dia. Double Flanged Gate Valve, to BS 5163 - Hand Operated, EURO Series 20,Type 23, Saint GOBAIN PAM or approved equivalent (In chamber) (Mark D) | Nr | 1
5.5 | 400mm dia Flange Adaptor (Mark E) | Nr | 2
5.6 | 400mm dia Single Flanged Spigot Pipe, length 450mm (Mark F) | Nr | 1
5.7 | 400mm Dia. V.J Coupling (Mark J) | Nr | 1
5.8 | 400mm dia. Double Flanged Pipe, length 5500mm with Puddle Flanges at 500mm and at 3470mm from one end (Mark G) | Nr | 1
5.9 | 400mm dia All Flanged Water Meter (Kent or Approved Equivalent) (Mark H) | Nr | 1
5.1 | 400mm dia Single Flanged Spigot Pipe, length 20000mm (Mark I) | Nr | 1
Wash water outlet Ferrous Pipes Fittings & Valves
5.11 | 300mm dia. Special Flanged Bellmouth, 415mm length, with Puddle Flange 170mm from the Bellmouth End (Mark A) | Nr | 1
5.12 | 300mm dia. 90° Double Flanged Short Radius Bends (Mark B) | Nr | 2
5.13 | 300mm dia. Double Flanged Pipe, length 5500mm with Puddle Flange 5050mm from one end (Mark C) | Nr | 1
5.14 | 300mm dia. Double Flanged Gate Valve, to BS 5163 - Hand Operated, EURO Series 20,Type 23, Saint GOBAIN PAM or approved equivalent (In chamber) (Mark D) | Nr | 1
5.15 | 300mm dia Flange Adaptor (Mark E) | Nr | 2
5.16 | 300mm dia Single Flanged Spigot Pipe, length 10000mm (Mark F) | Nr | 1
Overflow Ferrous Pipe Fittings
5.17 | 150mm dia. Flanged Spigot Pipe 1000mm length, with Puddle Flange at 120mm from Spigot End (Mark 1) | Nr | 1
5.18 | 150mm dia. 30° Double Flanged Bend (Mark 2) | Nr | 1
5.19 | 150mm dia. Flanged Spigot Pipe 2650mm length, with end bevelled (Length cut to suit on site). (Mark 3) | Nr | 1
Washout Ferrous Pipe Fittings
5.2 | 200mm dia. Flanged Spigot Pipe 5400mm length, with Puddle Flange at 120mm from Spigot End (Mark 4) | Nr | 1
5.21 | 200mm dia. Flanged Spigot Pipe 5400mm length, with Puddle Flange at 120mm from Spigot End (Mark 5) | Nr | 1
5.22 | 200mm dia. Double Flanged Gate Valve, Hand Operated to BS 5163, EURO 20 Series Type 23 (short face to face) or approved equivalent (Mark 6) | Nr | 1
5.23 | 200mm dia. Single Flanged 90° bend (Cut to suit on site) (Mark 7) | Nr | 1
6 | PIPEWORK - SUPPORTS AND PROTECTION, ANCILLARIES TO LAYING AND EXCAVATION
Provide and place:
6.1 | Mass Concrete Class 15/20 surround to washout pipe diameter 200mm to pipes; pipe nominal bore 250mm -450mm | m | 6
6.2 | -Ditto - but outlet pipe, diameter 400mm | m | 6
Concrete Class 20/20 in Stools and Thrust blocks
6.3 | Nominal bore 200 - 400mm; volume n.e. 0.1m³ | Nr | 1
7 | MISCELLANEOUS METALWORK
Rate to include supply and fixing, inclusive of foundations where applicable
7.1 | Galvanised mild steel internal ladders with stringers returned to form handrails | m | 6
PAGE TOTAL CARRIED TO BILL COLLECTION PAGE
7.2 | Lockable mild steel checkered plate 1020mm x 1020mm covers for access manholes and overflow chambers. | Nr | 3
8 | MISCELLANEOUS WORK
8.1 | Provide and fix vent pipes | Nr | 3
8.2 | Provide & lay 300mm wide x 12mm thick rubberoid layer between wall & roof slab. | m | 48
8.3 | Provide all materials and construct a 1800x1800x3200 deep reinforced Concrete Scour and Overflow Chamber | Nr | 1
8.4 | Provide all materials and construct a 2500x2500x2700mm deep Masonry Outlet Valve Chamber | Nr | 1
8.5 | Provide all materials and construct a 1500x1500x2700mm deep masonry Meter Chamber | Nr | 1
PAGE TOTAL CARRIED TO BILL COLLECTION PAGE

## Collection Sheet 3.5
TETU-AGUTHI WATER SUPPLY PROJECT
BILL No. 3.5
PAGE TOTALS COLLECTION SHEET
Amount
Kshs.
Page Total, Page 1 of 6
Page Total, Page 2 of 6
Page Total, Page 3 of 6
Page Total, Page 4 of 6
Page Total, Page 6 of 6
Page Total, Page 6 of 6
Bill No. 3.5 Total Exclusive of VAT Carried to Section 3 Summary Sheet

## Chlorine building
TETU-AGUTHI WATER SUPPLY PROJECT
BILL No. 3.6
CHLORINE STORAGE AND MIXING BUILDING
ITEM | DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
No. |  |  |  | (Kshs) | (Kshs)
1 | SUBSTRUCTURES (PROVISIONAL)
Excavations and Earthworks
The rates shall include for all strutting, shuttering,stabilising the excavation faces and keeping the excavation free of water by pumping, bailing or other means
Bulk excavations and top soil stripping for all structures are measured under Bill No. 3/4.10 - Site and Ancillary Works
Excavate below stripped level for foundations in common material, part backfill after construction and remainder, cart away to tips or use as fill on site, all as directed by the Engineer
Excavate 0.00-1.50m deep starting from stripped level to receive :-
1.1 | Foundations | m3 | 78
1.2 | Scour Chamber | m3 | 9
Extra over excavation in any position for:-
1.3 | Excavating in compacted gravel or decomposed rock | m3 | 6
1.4 | Excavating in soft rock or hard material | m3 | 13
Approved selected Filling
1.5 | Fill and ram selected excavated materials around foundations and buildings | m3 | 14
Approved filling as described:-
1.6 | Provide and deposit approved imported murram in maximum 150mm thick layers in making up levels over 300mm thick including achieving satisfactory compaction | m3 | 9
1.7 | Provide and deposit approved hardcore fill material 300mm thick in making up levels including achieving satisfactory compaction | m2 | 29
1.8 | Provide, lay and level out, 50mm thick fine crushed stone, sand or gravel blinding to surface of filling, including watering and rolling to achieve satisfactory compaction | m2 | 29
Disposal of Surplus Spoil:-
1.9 | Cart away surplus excavated materials to an approved dumping site | m3 | 73
Anti-Termite Treatment
1.1 | Chemical anti-termite treatment to surface of filling with an approved insecticide | m2 | 29
Damp-proof Membrane
1.11 | 500 Gauge polythene sheeting, laid over hardcore in two layers | m2 | 29
PAGE TOTAL CARRIED TO BILL COLLECTION PAGE
Concrete Work:
Mass Concrete Class 15/20mm maximum aggregate as described in:-
1.12 | 75mm Thick blinding under foundation concrete | m2 | 3
Guaranteed Strength Reinforced Concrete Class 25/20mm maximum aggregate as described in:-
1.13 | Strip Footing | m³ | 6
1.14 | Combined Footing and Columns | m3 | 6
Reinforcement
Provide and Fix High Tensile Steel Reinforcement to SRN 127 including cutting, bending, propping with spacers and tying as specified :-
1.15 | Reinforcement, all diameters | Kg | 1500
Formwork
Provide and fix shuttering including propping, strutting and striking, all as specified
Sawn Formwork - Class F1 Finish:-
1.16 | Vertical sides of Combined Footings and columns in foundations | m2 | 56
Wrot Formwork - Class F3 Finish:-
1.17 | Vertical sides of Combined Footings and columns in foundations | m2 | 28
SUPERSTRUCTURE
2 | CONCRETE, FORMWORK, REINFORCEMENT
Guaranteed Strength Reinforced Concrete Class 25/20mm as described in:
2.1 | 150mm thick Ground Floor Slab | m3 | 2
2.2 | 300mm thick Ground Floor Slab | m3 | 7
2.3 | 200mm thick First Floor Slab | m3 | 7
2.4 | 250mm Thick channel walls | m3 | 2
2.4 | 200mm thick Mixing Platform Slab | m3 | 2
2.5 | 200mm thick Tank Base Slab | m3 | 2
2.5 | 150mm Thick suspended ramp laid to slope not exceeding 15 degrees from horizontal | m3 | 10
2.6 | 200mm Thick Tank Walls | m3 | 7
2.7 | 150mm Thick Tank Walls | m3 | 1
2.8 | Provide all materials and form scour and dosing pipework channels with 150mm thick RC walls internal size 300mm wide x 150mm deep in concrete floor slab including forming rebate 50mm wide x 50mm deep to top inner edges of channel wall to receive precast concrete cover slabs. | m2 | 9
2.9 | Doser Platforms | m3 | 1
PAGE TOTAL CARRIED TO BILL COLLECTION PAGE
2.10 | Columns | m3 | 2
2.11 | Beams | m3 | 7
2.12 | External and Internal Stairs, Stair Landings and Stair Beams | m3 | 4
2.13 | Labour and material in forming lip in mixing tank concrete walls and partitions, lip 75mm wide x 150mm high with 75 x 75mm chamfered bottom edge | m | 5
Reinforcement
Provide and Fix High Tensile Steel Reinforcement to SRN 127 including cutting, bending, propping with spacers and tying as specified :-
2.14 | Reinforcement, all diameters | Kg | 2000
Formwork
Provide and fix shuttering including propping, strutting and striking, all as specified
Sawn Formwork - Class F1 Finish :-
Horizontal and Sloping Formwork
2.15 | Soffit of 200mm thick Mixing Platform Slab | m2 | 8
2.23 | Raking open string edge of staircase 325mm (extreme) high including cutting bottom edge to profile of treads and risers | m | 2
2.16 | Soffit of Doser Platfom | m2 | 2
2.17 | Soffit of External Stairs and Landings | m2 | 9
Wrot Formwork - Class F3 Finish :-
Vertical Formwork
2.18 | Sides of 150mm thick Ground Floor Slab | m2 | 2
2.19 | Sides of 300mm thick Ground Floor Slab | m2 | 5
2.21 | Sides of 200mm thick First Floor Slab | m2 | 5
2.22 | Sides of 200mm thick Tank Base Slab | m2 | 3
2.23 | Sides of 200mm Thick Tank Walls | m2 | 60
2.24 | Sides of 150mm Thick Tank Walls | m2 | 1
2.25 | Sides of Doser Platforms | m2 | 1
2.26 | Columns | m2 | 58
2.27 | Beams | m2 | 50
Horizontal and Sloping Formwork
2.28 | 200mm thick First Floor Slab Soffit | m2 | 36
2.29 | Sloping Soffit of Staircase | m2 | 7
Precast Reinforced Concrete Class 25/20
2.3 | 50mm thick cover slabs size 280mm long x 280mm wide for the Scour and Dosing Channels | m2 | 3
PAGE TOTAL CARRIED TO BILL COLLECTION PAGE
2.31 | 600 x 600 x 50mm thick precast concrete paving slabs around the building laid on and including 50mm thick bed of sand and jointing and pointing in cement mortar | m2 | 24
2.32 | 900 x 900 x 50mm thick cover slab for the Scour Chamber | m2 | 1
3 | WALLING
Selected Machine Dressed Natural Stone Block Walling, Reinforced with 20 swg Hoop Iron at every alternate courses, and Bedded, Jointed in Cement Mortar (1:3):-
3.1 | 200mm Thick walling | m2 | 90
Labours
3.2 | Extra over walling for ruled horizontal | m2 | 90
Damp Proof Membrane
3.3 | Bituminous felt damp-proof course under 200mm wide walls | m | 23
Precast Concrete Louvre Block Walling :-
3.4 | 200mm Thick louvre block walling with twin section with plastic coated coffee tray wire sandwiched between sections | m2 | 11
Dressed Stone Cills
3.5 | 200mm Thick x 275mm wide dressed stone cill bedded, jointed and pointed in cement mortar on top of 200mm wall | m | 9
4 | ROOF COVERINGS
Concrete, single lap interlocking roof tiles on and including sawn cypress (Grade 2) battens size 40 x 40mm pressure impregnated with approved preservative:-
4.1 | Roof tiles | m2 | 53
Extra over roofing tiles for:-
4.2 | Ridge capping including bedding and pointing in cement sand (1:4) mortar with colouring to match colour of tiles | m | 8
4.3 | Filled ends of ridge capping | Nr | 2
4.4 | 28 Gauge galvanized plain sheeting laid in two layers as underlay and nailed to rafters | m2 | 53
4.5 | Fair raking cutting roofing tiles | m | 21
4.6 | Fair raking cutting corrugated sheet roofing | m | 21
PAGE TOTAL CARRIED TO BILL COLLECTION PAGE
Carpentry
Roof Timbers
Double Pitch Roof Truss in Sawn Cypress Grade II Seasoned and Pressure Impregnated with Wood Preservative and timber joints with bolted and nailed connections to the Engineer's approval :-
5.1 | Equal scissor truss 6000mm clear span and 1100 mm high with 600 mm eaves projection, in 150mm x 50mm rafters and ceiling joists/Rafter tie | Nr | 4
Other Roof Members
Sawn Cypress Grade II Maximum Moisture Content 12% Seasoned and Pressure Impregnated with Wood Preservative and timber joints with bolted and nailed connections to the Engineer's approval:-
5.2 | 100 x 50mm Intermediate rafters | m | 49
5.3 | 150 x 50mm Purlins | m | 16
5.4 | 200 x 50mm Ridge board | m | 8
5.5 | 100 x 50mm Wall plate tied to wall with 20 s.w.g. hoop iron at 900mm centres | m | 25
5.6 | Scarfed joint to 200 x 50mm timber member | Nr | 1
5.7 | Scarfed joint to 150 x 50mm timber member | Nr | 2
Sundries
5.8 | Bed wall plate in cement mortar (1:3) | m | 25
Joinery
General Timbers
Wrot Prime Grade Cypress
5.9 | 250 x 40mm Fascia board | m | 29
6 | CEILING
12mm Thick Gypsum Board or approved Equivalenet Fixed to and including 50 x 50mm sawn cypress Grade 2 battens at 600mm centres in both directions complete with Gauge Jointing Material
6.1 | Ceiling laid to slope not exceeding 15 degrees fixed to underside of trusses | m2 | 37
6.2 | 12mm Cornice 50mm high laid to slope, plugged | m | 23
6.3 | Extra over ceiling lining for forming removable access trap door size 600 x 600mm with 100 x 38 mm sawn treated cypress trimming joists between tie beams,120 x 20mm (finished ) wrot cypress frame all round and 20mm blockboard removable panel set loose on top of framing | Nr | 1
PAGE TOTAL CARRIED TO BILL COLLECTION PAGE
7 | METALWORK
Steel Doors
Pressed Metal Louvre Doors
Supply and Fix the following Pressed Metal Louvre Doors with 100 x 50mm Stiles and Top Rails, 150 x 50mm Middle and Bottom Rails With Pressed Metal Infill Louvres and 100 x 50mm Pressed Metal Frames, Including Hinges, Pad Bolts and Tower Bolts, All To Manufacturer's Details, with one coat lead oxide primer complete with opening accessories including bedding and pointing around frames in cement mortar:-
7.1 | Double door size 1800 x 2400 mm high in two equal panels (D2) | Nr | 1
7.2 | Double door size 1200 x 2400 mm high in two equal panels (D2a) | Nr | 1
7.3 | Double door size 1800 x 2500 mm high in two equal panels | nr | 1
uPVC Casement Windows
Supply and Fix the following Standard Section PVC Casement Windows, including 4mm Thick Clear Sheet Glass glazed to Steel Casements with Putty, Complete with Opening Accessories, Including Building in Lugs to Jambs and Head and Water-Proofing and Filling Around Opening with Approved Compound; and Including Burglar-Proofing Fabricated from 12 x 12mm Mild Steel Square Bars at 150mm Centres Vertically and 150mm Horizontally and Fixed Internally to Surrounding Wall with 12mm Mild Steel Fish-Tailed Lugs at Maximum 600mm Centres; all Finished with Three Coats Oil Paint, :-
7.3 | Window size 1197 x 1197mm high in3 equal panels, with upper part having 2nr. fixed and 1nr. top-hung ventilator and lower half having 2nr. side hung panels opening outwards and 1nr. fixed panel (W2a) | Nr | 1
7.4 | Window size 1797 x 597mm high in 3 equal panels with 1 No. fixed and 2 No. top hung panels opening outwards (W5) | Nr | 2
7.5 | Window size 1197 x 597mm high in 2 equal panels, with 1 No. fixed and 1 No. top hung ventilator (W7) | Nr | 4
Balustrades and Railings
Balustrade Unit 1000mm High comprising 40mm Diameter Galvanised Pipe Top, Middle and Bottom Rails and 40mm Diameter Galvanised Pipe Balusters Spaced at Maximum 1000mm centres and bottom end bent, fanged and built into mortice in concrete, including all necessary Welding:-
7.6 | Raking Balustrade unit 9000mm long, 6000mm and 3000mm | m | 10
7.7 | Level Balustrade unit 6000mm long, 4500mm and 1500mm | m | 4
PAGE TOTAL CARRIED TO BILL COLLECTION PAGE
RENDERING
12.5mm Thick Cement and Sand Render as described externally on :-
7.8 | Columns | m2 | 24
7.9 | Horizontal sides and soffites of beams | m2 | 22
8 | PLASTERING
12.5mm Thick Gauged Cement Plaster as Described Internally on :-
8.1 | Concrete or blockwork | m2 | 145
8.2 | Reveals of openings | m2 | 5
8.3 | Sloping soffites of ramp not exceeding 15 degrees from horizontal | m2 | 19
8.3 | Sloping soffites of staircase | m2 | 7
8.5 | Raking open string edge of staircase 295mm (extreme) high | m | 2
Screeds
Bonded cement and sand (1:4) screed bed in one coat, well bonded to concrete base as described:-
8.4 | 38mm Thick screed laid level to receive Ceramic floor tiling | m2 | 79
8.5 | 12mm (minimum) Thick Cement and sand backing (1:4) with approved plasticiser to receive granito floor laid to treads and risers (measured separately) | m2 | 21
Bonded cement and sand (1:4) screed bed in one coat with approved hardener incorporated in the mix, well bonded to concrete base as described:-
8.6 | 38mm Thick screed laid level to receive epoxy lining (measured separately) | m2 | 47
8.7 | 150 x 20mm Thick skirting with hardener laid with a square top edge and coved junction with floor finish | m | 39
Floor Tiling
Ceramic Floor Tiles :-
8.8 | Floor tiles laid on screed (measured separately) with straight joints both ways | m2 | 79
8.9 | Tiles laid to risers and treads of steps on screed (measured separately) with straight joints both ways | m2 | 21
8.1 | Tiles laid as skirting 150mm high | m | 39
8.11 | Provide and fix 12mm thick Acrilin Tank Wall Tiles fixed with tile adhesive with straight joints both ways | m2 | 47
Water Based Epoxy Floor and Wall Coating as 'MASTERTOP 1110T' applied strictly in accordance with the Manufacturer's printed instruction :-
8.12 | Coating laid to mixing tanks floors, walls and partitions | m2 | 36
8.13 | Coating laid to vertical skirting or upstand surfaces | m2 | 39
PAGE TOTAL CARRIED TO BILL COLLECTION PAGE
9 | PAINTING AND DECORATING
Prepare, knot, prime, stop and apply three coats first quality gloss paint to wood surfaces
Externally on:-
9.1 | General surfaces of fascia boards | m2 | 11
Prepare, touch up primer and apply three coats gloss paint :
Externally on:-
9.2 | General surfaces of louvred metal doors (measured flat overall) | m2 | 15
9.3 | Surfaces of Balustrades and Railings | m | 11
Internally on:-
9.4 | General surfaces of louvred metal doors (measured flat overall) | m2 | 15
9.5 | Surfaces of Balustrades and Railings | m | 3
Prepare and Apply Three Coats Exterior Quality Plastic Emulsion Paint:-
Externally on:-
9.6 | Fair-faced vertical concrete columns | m2 | 24
9.7 | Fair-faced horizontal sides and soffites of beams | m2 | 22
Prepare and Apply Three Coats Interior Quality Plastic Emulsion Paint:-
Internally on:-
9.8 | Plastered concrete or blockwork | m2 | 145
9.9 | Ditto reveals of openings | m2 | 5
10.8 | Ditto sloping soffites of ramp not exceeding 15 degrees from horizontal | m2 | 19
9.1 | Ditto sloping soffites of staircase exceeding 15 degrees from horizontal | m2 | 7
10.1 | Ditto raking open string edge of staircase 295mm (extreme) high | m | 2
9.11 | Horizontal soffites of suspended slabs | m2 | 36
Prepare and Apply Three Washable Distemper as Described to:-
9.12 | Sloping soffites of suspended plasterboard ceilings | m2 | 37
10.13 | Ditto 100-200mm girth | m | 60
10 | CHLORINE / SODA ASH MIXING TANKS
Note: All technical details including type, material, specification, etc. to be submitted with Tender for all chemical mixing equipment and pipework. Non-submission of above requirement will result in equipment to be supplied to approval of the Engineer and the cost quoted will deem to include the required approved materials and equipment
10.1 | Provide and place 6mm stainless steel chemical dissolving tray | Nr | 3
PAGE TOTAL CARRIED TO BILL COLLECTION PAGE
Ranges for Chlorine / Soda Ash mixing tanks in Chemical Storage and Mixing Building
Supply all equipment to site, store, install, commission and maintain the following ranges and equipment, including all nuts, bolts, washers, packing etc.
10.2 | Three ranges complete of 25mm uPVC pipework for water supply to Chlorine and Soda Ash mixing tanks including for making connection to domestic water supply main | Item | L.S
10.3 | Three ranges complete of 80mm diameter uPVC pipes and fittings for outlet from Chlorine and Soda Ash mixing tanks to solution feed dosers | Item | L.S
10.4 | Three ranges complete of 80mm diameter uPVC pipes and fittings for overflow and for washout of Chlorine and Soda Ash mixing tanks Include for all anchoring and supporting of all pipework and fittings | Item | L.S
10.5 | Three ranges of pipework of 40mm diameter reinforced nylon pipe from Chlorine and Soda Ash mixing tanks; laid within Chlorine Dosing Channel to the Dosing Point | Item | L.S
Provide and fix approved "Epofloor" lining in accordance with the manufacturer's instructions (supplied by Robbialac Paints or approved equivalent)
10.6 | 5mm lining to bottom of mixing tanks | m2 | 9
10.7 | 5mm lining to internal sides of mixing tanks | m2 | 38
10.8 | Provide and fix gravity solution feed dosers of capacity upto 50ml/s of Opados Type or approved equivalent complete with valves and connections for Chlorine and Soda Ash Dosing. | Nr | 3
10.9 | Provide and fix 300mm diameter exhaust extractor fan to be fixed in the Chlorine and Soda Ash storage and mixing room | Nr | 2
10.10 | Provide and fix electrically driven mixers for Chlorine and Soda Ash mixing tanks. The shaft and impellers to be of non-corrosive material driven by electric motor (2.0 kw). Include for fixing on tanks | Nr | 3
Flow Meter
11.11 | Supply, install and commission ultrasonic flow meter to measure and record flow in treated water open channel. The instrument should be complete with measurement of instantaneous flow and totalised flow. The cost should include for fixing brackets, battery backup, sensors / integrator, cables, flow connector and calibration. | nr | 1
11.12 | Provide and install remote indicator located in the Administration building of instantenous flow and total flows from the treated water flow meter. Include for control cables, ducting, trenching for installation of remote indicators. Maximum length 100m from meter to remote location of indicator | nr | 1
11 | CHAMBERS
11.1 | Provide all materials and form Scour Chamber internal size 1200mm long x1200mm wide x 1000mm deep made out of 150mm thick reinforced concrete class 25/20 base slab and 200mm thick masonry walls including forming rebate 50mm wide x 50mm deep to top inner edges of the chamber wall to receive a precast concrete cover | Nr | 1
12.1 | Form 200mm x 150mm deep dosing pipework channel and scour/overflow channel in base slab of chlorine mixing room. Apply 3 coats of approved epoxy paint to internal surfaces of channels | m | 12
12.2 | Form rebate 50mm x 50mm for precast concrete cover slabs over the dosing pipework and scour/overflow channels. Apply 3 coats of approved epoxy paint to surfaces of rebates | m | 24
12.3 | Provide and fix precast concrete slabs 500mm x 290mm x 45mm thick, each slab coated with 3 layers of approved epoxy paint | nr | 24
PAGE TOTAL CARRIED TO BILL COLLECTION PAGE

## Collection Sheet 3.6
TETU-AGUTHI WATER SUPPLY PROJECT
BILL No. 3.6
PAGE TOTALS COLLECTION SHEET
Amount
(Kshs)
Page Total, Page 1 of 9
Page Total, Page 2 of 9
Page Total, Page 3 of 9
Page Total, Page 4 of 9
Page Total, Page 5 of 9
Page Total, Page 6 of 9
Page Total, Page 7 of 9
Page Total, Page 8 of 9
Page Total, Page 9 of 9
Bill No. 3.6 Total Exclusive of VAT Carried to Section 3 Summary Sheet

## Back wash Pump House
TETU-AGUTHI WATER SUPPLY PROJECT
BILL No. 3.7
TREATMENT WORKS - BACK WASH WATER PUMP HOUSE
ITEM | DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
No. |  |  |  | (Kshs) | (Kshs)
SUB-STRUCTURE
1 | EXCAVATION
The rates shall include for all strutting, shuttering, stabilising the excavation faces, and keeping the excavation free of water by pumping, bailing or other means.
Bulk excavations and top soil stripping for all structures are measured under Bill No. 3.12 (Site & Ancillary Works).
Excavate below stripped level to formation level in common material, part backfill after construction and remainder, cart away to tips or use as fill on site, all as directed by the Engineer.
1.1 | Maximum depth n.e. 1.0 m | m3 | 110
1.2 | -Ditto- but maximum depth 1.0 m to 2.0 m | m3 | 60
1.3 | -Ditto- but maximum depth 2.0 m to 3.0 m | m3 | 2
Extra Over Excavation in Any Position for:-
1.4 | Excavating in rock Class "A" | m3 | 11
1.5 | Excavating in rock Class "B" | m3 | 18
1.6 | Excavating in rock Class "C" | m3 | 7
Approved Selected Filling as Described:-
1.7 | Provide and deposit approved selected fill in maximum 150mm thick layers in making up levels including achieving satisfactory compaction. Rate to include performing necessary compaction tests. | m3 | 20
1.8 | Provide, lay and level out fine crushed stone, sand or gravel blinding 50mm thick to surface of filling, including watering and rolling to achieve satisfactory compaction. | m2 | 54
1.9 | Fill with approved hardcore in a 300mm thick layer including achieving satisfactory compaction. | m2 | 54
Disposal of Surplus Spoil:-
1.1 | Cart away surplus excavated materials to an approved dumping site | m3 | 152
Anti-Termite Treatment
1.11 | Chemical anti-termite treatment to surface of filling with an approved insecticide. | m2 | 54
Damp-Proof Membrane
1.12 | 500 Gauge polythene sheeting, laid over hardcore in two layers | m2 | 54
PAGE TOTAL CARRIED TO SECTION COLLECTION SHEET
CONCRETE WORK
Mass Concrete Class 15/20mm Maximum Aggregate as Described in:-
1.13 | 75mm Thick blinding under the walls strip footings, column bases and over hardcore | m2 | 75
Guaranteed Strength Reinforced Concrete Class 25/20mm Maximum Aggregate as Described in:-
1.14 | 400mm Thick Base Slab | m3 | 20
1.15 | 150mm Thick Base Slab | m3 | 5
1.16 | 300mm Thick Column Bases and Wall Strip Footings | m3 | 2
1.17 | Isolated columns and piers in foundations | m3 | 1
1.18 | Pump Plinth size 1850mm long x 750mm wide x 300mm deep | m3 | 2
1.19 | Air Blower Plinth size 2500mm long x2150mm wide x 300mm deep | m3 | 4
Builders Work
1.2 | Drainage sump internal size 400mm long x400mm wide x 400mm deep made out of 150mm thick reinforced concrete base and walls including forming rebate 50mm wide x 75mm deep to top inner edges of sump wall to receive chequer plate cover (m.s.) and including all necessary excavation, disposal and formwork. | Nr | 1
1.21 | Form cable duct internal size 200mm wide x 250mm deep in concrete floor slab including forming rebate 50mm wide x 75mm deep to top inner edges of channel wall to receive chequer plate cover (m.s.) | m | 14
1.22 | Form drainage channel internal size 150mm wide and depth varying from 150mm to 200mm deep in concrete floor slab including forming rebate 50mm wide x 75mm deep to top inner edges of channel wall to receive mild steel grating cover (m.s.) | m | 6
1.23 | Provide all materials and install a 100mm Dia. Upvc drainage pipe cast into floor slab. | m | 2
1.24 | Form pocket internal size 1900mm long x 800mm wide x 175mm deep in base slab to receive pump plinth (R.C.) including all the necessary formwork | Nr | 2
1.25 | Form pocket internal size 2450mm long x 2200mm wide x 175mm deep in concrete topping to receive air blower plinth (R.C.) including all the necessary formwork | Nr | 2
Guaranteed Strength Reinforced Concrete Class 25/20mm Maximum Aggregate as Described in:-
1.26 | 100mm Thick ramp laid to slope not exceeding 15 degrees from horizontal | m3 | 1
1.27 | Extra over for tamping concrete whilst still green to make ribbed finish of the ramp area. | m2 | 5
PAGE TOTAL CARRIED TO SECTION COLLECTION SHEET
Fabric Reinforcement No. A142 Mesh Size 150 x 150mm Weighing 2.22 kgs Per m2 , Including Bends, Tying Wire and Distance Blocks:-
1.28 | Fabric reinforcement with minimum 150mm wide side and end laps, laid in bed | m2 | 5
Provide and Fix High Tensile Steel Reinforcement to SRN 127 including Cutting, Bending, Propping With Spacers and Tying as Specified :-
1.29 | Reinforcement, all diameters | Kg | 3300
FORMWORK
Provide and Fix Shuttering Including Propping, Strutting and Striking, all as Specified
Sawn Formwork - Class F1 Finish:-
1.3 | Sides of 400mm thick pump house base slab | m2 | 11
1.31 | Sides of 150mm thick pump house base slab | m2 | 1
1.32 | Sides of 300mm column bases and columns in the foundations | m2 | 10
1.33 | Sides of 300mm Walls Strip footings - Pump house walls | m2 | 20
1.34 | Drainage sump internal size 400mm long x400mm wide x 400mm deep made out of 150mm thick reinforced concrete base and walls including forming rebate 50mm wide x 75mm deep to top inner edges of sump wall to receive chequer plate cover (m.s.) and including all necessary excavation, disposal and formwork | m2 | 1
1.35 | Form cable duct internal size 200mm wide x 250mm deep in concrete floor slab including forming rebate 50mm wide x 75mm deep to top inner edges of channel wall to receive mild steel grating cover (m.s.) | m2 | 7
1.36 | Form drainage channel internal size 150mm wide and depth varying from 150mm to 200mm deep in concrete floor slab including forming rebate 50mm wide x 75mm deep to top inner edges of channel wall to receive mild steel grating cover (m.s.) | m2 | 3
Wrot Formwork - Class F3 Finish:-
1.37 | Edges of Pump Plinth size 1850mm long x 750mm wide x 300mm deep not exceeding 300mm wide | m | 11
1.38 | Edges of Air Blower Plinth size 2400mm long x 2150mm wide x 300mm deep not exceeding 300mm wide | m | 20
RENDERING
15mm Cement and sand (1:4) render to plinths, finished with a wood float
1.39 | Pump Plinth size 1850mm long x 750mm wide x 300mm deep including pocket in base slab | m2 | 5
1.4 | Air Blower Plinth size 2400mm long x 2150mm wide x 300mm deep including pocket in base slab | m2 | 14
PAGE TOTAL CARRIED TO SECTION COLLECTION SHEET
Bonded Cement and Sand (1:4) Screed Bed in One Coat with Approved Hardener incorporated in the Mix, Well Bonded to Concrete Base as Described:-
1.41 | 40mm Thick paving with wood float finish on pump house slab | m2 | 54
PAINTING AND DECORATING
1.42 | Prepare and apply two coats of bituminous paint on rendered plinth walls | m2 | 19
1.43 | Provide and apply approved industrial Epoxy floor paint on the Pump House Floor. | m2 | 35
Damp-proof course:
Bituminous Felt Damp-Proof Course as Described:-
1.44 | 200mm Wide under walls | m | 30
Joint Filler
1.45 | 20mm Thick resin bonded cork filler between 1850 x 750 x 300mm pump plinth and 250mm thick floor slab sealed with 25mm deep bitumen | m2 | 5
1.46 | 20mm Thick resin bonded cork filler between 2400 x 2150 x 300mm air blower plinth and 250mm thick floor slab sealed with 25mm deep bitumen | m2 | 14
Walling
Natural Stone Block Walling, Medium Chisel Dressed, Reinforced with 20 swg Hoop Iron at every third course, and Bedded, Jointed and Pointed in Cement Mortar (1:4):-
1.47 | 200 mm Walling | m2 | 20
SUPERSTRUCTURE
CONCRETE WORKS
Guaranteed Strength Reinforced Concrete Class 25/20mm as Described in:
1.48 | Upstand for the control panel | m3 | 1
1.49 | Columns | m3 | 2
1.5 | Beams | m3 | 3
Precast Concrete Paving Slabs
1.51 | Slabs size 600 x 600 x 50mm Thick laid on and including 50mm thick bed of sand and jointing and pointing in cement mortar | m2 | 50
REINFORCEMENT
Provide and Fix High Tensile Steel Reinforcement to SRN 127 including Cutting, Bending, Propping with Spacers and Tying as Specified :-
1.52 | Reinforcement, all diameters | kg | 720
PAGE TOTAL CARRIED TO SECTION COLLECTION SHEET
FORMWORK
Provide and Fix Shuttering Including Propping, Strutting and Striking, all as Specified.
1.53 | Upstand for the control panel, columns and beams in the superstructure. | m2 | 35
WALLING
Selected Machine Dressed Natural Stone Block Walling, Reinforced with 20 swg Hoop Iron at Every Third Courses, and Bedded, Jointed and Pointed in Cement Mortar (1:5):-
1.54 | 200mm Thick walling | m2 | 60
Labours
1.55 | Extra over walling for ruled horizontal and flush vertical joints | m2 | 60
Precast Concrete Cills
1.56 | 200mm Thick x 275mm wide precast concrete cill bedded, jointed and pointed in cement mortar on top of 200mm wall | m | 8
PLASTERING
1.57 | 12.5mm thick cement gauged plaster internally on blockwork surfaces | m2 | 70
RENDERING
1.58 | 12.5mm thick cement and sand rendering externally on concrete surfaces | m2 | 25
METALWORK
Rates to include for Provision of all Material, Fabrication and Fixing
Floor Gratings
1.59 | Mild steel grating drain channel cover 240mm wide x 5900mm long made out of 16mm round m.s transverse bars welded at 20mm spacing to 16mm round m.s longitudinal bars welded to 38 x 38 x 6mm thick m.s angles | m2 | 2
1.6 | Mild steel chequer plate cover for cable duct internal size 200mm wide x 250mm deep | m2 | 3
UB Gantry
1.61 | Provide and fix Gantry girder made out of 356 x 174 x 45 kg/m UB. Include for 1000kg capacity chain block mounted on roller bracket on the gantry, fixing of gantry to concrete beams of pump house with 16mm bolts, etc., all. | Nr | 1
PAGE TOTAL CARRIED TO SECTION COLLECTION SHEET
Steel Doors
Pressed Metal Louvre Doors
Supply and Fix the Following Pressed Metal Louvre Doors with 100 x 50mm Stiles and Top Rails, 150 x 50mm Middle and Bottom Rails With Pressed Metal Infill Louvres and 100 x 50mm Pressed Metal Frames, Including Hinges, Pad Bolts and Tower Bolts, All To Manufacturer's Details, With Three Coats Gloss Paint Complete With Opening Accessories Including Bedding and Pointing Around Frames in Cement Mortar:-
1.62 | Double door size 1800 x 2400 mm high in two equal panels | Nr | 1
Steel Casement Windows
Supply and Fix the following Standard Section Steel Casement Windows, including 4mm Thick Clear Sheet Glass glazed to Steel Casements with putty, complete with the following, all finished with three coats oil paint:-
- Opening accessories, including building in lugs to jambs and head and water-proofing and filling around opening with approved compound
- Solid Timber Window Board, 200mm wide x 25mm thick, exposed edge with bull-nose finish
- Burglar-Proofing Fabricated from 12 x 12mm Mild Steel Square Bars at 150mm Centres Vertically and 150mm Horizontally and Fixed Internally to Surrounding Wall with 12mm Mild Steel Fish-Tailed Lugs at Maximum 600mm Centres;
1.63 | Window size 1797 x 1197mm high in 3 equal panels with upper part having 2 No. fixed and 1 No. top hung ventilator,and lower half having 2 No. side-hung panels opening outward and 1 No. fixed panel (W1) | Nr | 2
1.64 | Window size 1797 x 597mm high in 3 equal panels, with upper part having 2 no. fixed & 1 no. top - hung ventillator & lower half having 2 no. side hung panel openning outwards, and 1 no. fixed panel (W5) | Nr | 2
PVC Gauze Screen set on and including a Timber Framing all Round and Fixing to Wall :-
1.65 | Gauze size 1275 x 600mm high | Nr | 4
1.66 | Gauze size 1800 x 870mm high | Nr | 2
PAINTING AND DECORATING
Prepare and Apply Three Coats Exterior Quality Plastic Emulsion Paint:-
Externally on:-
1.67 | Fair-faced concrete surfaces | m2 | 25
Prepare and Apply Three Coats Interior Quality Plastic Emulsion Paint:-
Internally on:-
1.68 | Plastered blockwork and concrete surfaces | m2 | 95
PAGE TOTAL CARRIED TO SECTION COLLECTION SHEET
1.69 | Allow for painting of all pipework within the Pump House with 3 coats of approved super gloss paint applied on 1 coat primer | Item | L.S
Prepare and Apply Three Coats Washable Distemper as Described to:-
1.7 | Horizontal soffites of suspended chipboard or plasterboard ceilings | m2 | 54
ROOF COVERINGS
Concrete, Single Lap Interlocking Roof Tiles on and Including Sawn Cypress (Grade 2) Battens Size 40 x 40mm Pressure Impregnated with Approved Preservative:-
1.71 | Roof tiles | m2 | 90
Extra Over Roofing Tiles for:-
1.72 | Ridge capping including bedding and pointing in cement sand (1:4) mortar with colouring to match colour of tiles | m | 3
1.73 | Hip capping ditto | m | 18
1.74 | Filled ends of ridge capping or hip capping | Nr | 6
1.75 | Fair raking cutting roofing tiles | m | 18
1.76 | Gauge 28 galvanised plain sheets as laid as underlay and nailed to rafters (m²) | m2 | 90
CARPENTRY AND JOINERY
Carpentry
Roof Trusses
Double Pitch Roof Truss With 600mm Eaves Projection, in 150 x 50mm Rafters, Ceiling joists, Struts and Ties in Sawn Cypress Grade II Seasoned and Pressure Impregnated with Wood Preservative and timber joints with Bolted and Nailed Connections to the Engineer's Approval :-
1.77 | Equal truss 6600mm clear span and 1560mm high at 1500mm c/c | Nr | 3
Other Roof Members
Sawn Cypress Grade II Maximum Moisture Content 12% Seasoned and Pressure Impregnated with Wood Preservative and Timber Joints With Bolted and Nailed Connections to the Engineer's Approval:-
1.78 | 150 x 50mm Intermediate and hip rafters | m | 95
1.79 | 150 x 75mm Purlins | m | 19
1.8 | 180 x 50mm Ridge board | m | 3
1.81 | 100 x 50mm Wall plate tied to wall with 20 s.w.g. hoop iron at 900mm centres and bedded in cement mortar (1:4) on top of wall | m | 30
PAGE TOTAL CARRIED TO SECTION COLLECTION SHEET
Joinery
General Timbers
Wrot Prime Grade Cypress, Including Finishing With Three Coats First Quality Gloss Paint :-
1.82 | 250 x 40mm Fascia board, fixed with screws | m | 37
2 | CEILING
12mm Thick Approved Chipboard to BS 2604, Part 2, density 480-640kgs, per Square Meter in Sheets Size 2400 x 1200mm Fixed to and Including 50 x 50mm Sawn Cypress Grade 2 Battens at 600mm Centres in Both Directions Complete with Gauge Jointing Material
2.1 | Horizontal ceiling fixed to underside of trusses | m2 | 60
2.2 | 12mm Cornice 50mm high, plugged | m | 30
2.3 | Extra over ceiling lining for forming removable access trap door size 600 x 600mm with 100 x 38 mm sawn treated cypress trimming joists between tie beams,120 x 20mm (finished ) wrot cypress frame all round and 20mm blockboard removable panel set loose on top of framing. | Nr | 1
Builders Work in Connection with Electrical Installations
2.4 | Allow for cutting and leaving all necessary holes, notches, mortices, sinkings and chases both in the structure and its finishes and for all making good in connection with concealed conduits or cables | Item | L.S
PIPEWORK AND FITTINGS
Rate to include for Supply, Transport to Site, Store, Install, Test & Commission. Include for Excavation & Backfilling of Pipe Trenches Where Applicable. Include Jointing Material, Bolts, Gaskets, Packing, Jointing Glues, etc., As Applicable
Backwash Pumps - Suction Main (Approved Lined Ferrous Pipe Fittings)
2.5 | 300mm dia. special 900 bend, one end flanged, other end bellmouth shaped (Mark A) | Nr | 1
2.6 | 300mm dia. all flanged pipe, length 2000mm (Mark B) | Nr | 1
2.7 | 300mm dia. all flanged pipe 1400mm long with puddle flange at 450mm from one end (Mark C) | Nr | 1
2.8 | 300 mm dia. flange spigot pipe 1330mm long (Mark C1) | Nr | 1
2.9 | 300mm dia. Flanged adaptor (Mark C2) | Nr | 1
2.1 | 300mm x 300mm dia. all flanged tee (Mark D) | Nr | 1
2.11 | 300mm dia. all flanged pipe, length 800mm (Mark E) | Nr | 2
2.12 | 300mm x 150mm dia. special all flanged level invert tee (Mark F) | Nr | 2
2.13 | 300mm dia. blank flange (Mark G) | Nr | 2
PAGE TOTAL CARRIED TO SECTION COLLECTION SHEET
2.14 | 150mm dia. all flanged pipe, length 444mm (Mark H) | Nr | 2
2.15 | 150mm dia. all flanged pipe 600mm long with puddle flange at 400mm from one end (Mark I) | Nr | 2
2.16 | 150 mm dia. flange spigot pipe 795mm long (Mark J) | Nr | 2
2.17 | 150mm dia. Flanged adaptor (Mark K) | Nr | 2
2.18 | 150mm dia. all flanged gate valve to BS 5163 (Mark L) | Nr | 2
2.19 | 150mm dia. all flanged special 90º bend (Mark M) | Nr | 2
2.2 | 150mm x 100mm dia. all flanged eccentric taper (Mark N) | Nr | 2
Backwash Pumps - Delivery Main (Approved Lined Ferrous Pipe Fittings)
2.21 | Special 100mm x 65mm all flanged concentric taper with 25mm dia. Male threaded tapping for pressure gauge (Mark 1) | Nr | 2
2.22 | 25mm dia. pressure gauge (pressure class up to 10 bars) - Hunter or approved equivalent (Mark 2) | Nr | 2
2.23 | 100mm dia. all flanged 90° bend (Mark 3) | Nr | 4
2.24 | 100mm dia. all flanged free acting check valve (Non return valve (Mark 4) | Nr | 2
2.25 | 100mm dia. all flanged gate valve to BS 5163 (Mark 5) | Nr | 2
2.26 | 100mm dia. flange adaptor (Mark 6) | Nr | 4
2.27 | 100mm dia. flanged spigot pipe, length 640mm (Mark 7) | Nr | 2
2.28 | 100mm dia. all flanged pipe 800mm long with puddle flange at 250mm from one end (Mark 8) | Nr | 2
2.29 | 100mm x 50mm dia. all flanged radial tee (Mark 9) | Nr | 2
2.3 | 50mm dia. Single orifice air valve with built in isolating valve (Mark 10) | Nr | 2
2.31 | 150mm dia. flanged spigot pipe 1980mm long (Mark 11) | Nr | 2
2.32 | 150mm x 100mm dia. all flanged radial tee (Mark 12) | Nr | 2
2.33 | 150mm dia. blank flange (Mark 13) | Nr | 1
2.34 | 150mm dia. all flanged pipe, length 2720mm (Mark 14) | Nr | 1
2.35 | 150 mm dia. flange spigot pipe 1200mm long (Mark 15) | Nr | 1
2.36 | 150mm dia.V.J. Coupling (Mark 16) | Nr | 1
Airwash - Delivery Main (Approved Lined Ferrous Pipe Fittings
2.37 | 150mm dia. plain ended pipe, length 200 mm (Cut to suit on site) (Mark 1) | Nr | 2
2.38 | 150mm dia. flanged spigot 90º bend (Mark 2) | Nr | 2
PAGE TOTAL CARRIED TO SECTION COLLECTION SHEET
2.39 | 150mm dia. flange adaptor (Mark 3) | Nr | 2
2.4 | 150mm dia. flanged spigot pipe, length 475mm (Mark 4) | Nr | 2
2.41 | 150mm dia. flanged butterfly valve (Mark 5) | Nr | 4
2.42 | 150mm x 150mm x 150mm dia. all flanged radial tee (Mark 6) | Nr | 2
2.43 | 150mm dia. blank flange (Mark 7) | Nr | 1
2.44 | 150mm dia. all flanged pipe, length 2470mm (Mark 8) | Nr | 1
2.45 | 150mm dia. all flanged 90° bend (Mark 9) | Nr | 1
2.46 | 150mm dia. all flanged pipe, length 1200mm with puddle flange at 290mm from one end (Mark 10) | Nr | 1
2.47 | 150mm dia. flanged spigot pipe, length 1200mm (Mark 11) | Nr | 1
2.48 | 150mm dia.V.J. Coupling (Mark 12) | Nr | 1
3 | PUMPS
Backwash Pumps
3.1 | Supply, transport to site, install, test and commission centrifugal pumps (1 duty, 1 standby) complete with motor, base plate, fixing bolts, grouting, etc., for the following characteristics: Flow 91m3 per hour, dynamic head 20m, KSB Etarnorm 80-250 or approved equivalent. | Nr | 2
4 | AIR BLOWERS
4.1 | Supply, transport to site, install, test and commission air blowers (1 duty, 1 standby); Include for electric motor, air receiver, pressure gauge, pressure switch, safety valve, isolating valve, automatic moisture seperator with differential pressure gauge regulator, air drier, oil water filter and all piping and valvers KAESER or equivalent - capacity 30 m³/min (free air) | Nr | 2
PAGE TOTAL CARRIED TO SECTION COLLECTION SHEET

## Collection Sheet 3.7
TETU-AGUTHI WATER SUPPLY PROJECT
BILL No. 3.7
TREATMENT WORKS - BACK WASH WATER PUMP HOUSE
Amount
Kshs.
Page Total, Page 1 of 10
Page Total, Page 2 of 10
Page Total, Page 3 of 10
Page Total, Page 4 of 10
Page Total, Page 5 of 10
Page Total, Page 6 of 10
Page Total, Page 7 of 10
Page Total, Page 8 of 10
Page Total, Page 9 of 10
Page Total, Page 10 of 10
Bill No. 3.6 Total Exclusive of VAT Carried to Section 3 Summary Sheet

## Backwash water tank
TETU-AGUTHI WATER SUPPLY PROJECT
BILL No. 3.9
ELEVATED BACKWASH WATER TANK (150m³ )
ITEM | DESCRIPTION | UNIT | QUANTITY | RATE (Kshs) | AMOUNT (Kshs)
cts
1 | ELEVATED BACKWASH TANK & TOWER
1.1 | Supply and Transport to Site Pressed Steel Galvanised Steel Tank with Cover, minimum Net Storage Capacity 150m³ (size 7.32m x 6.1m x 3.66m) in accordance with Approved Specifications on and including 8m high galvanised steel U.B and U.C. section tower, including provision of Connections, Vents Base, Plates, Ladder and Platform on all 4 sides, etc. Note: Contractor to submit to the Engineer for approval, detailed design calculations and workshop drawings of all steel work from an approved and reputable Structural Steel Fabricator prior to fabrication and delivery of tank and tower. | Item | L.S
1.2 | Allow for the erection of Tank and Tower and all Assembling, Water Proofing, Welding, Drilling Holes, Cleats Bolts and Nuts, Cutting , Fixing Clamps, Ladder, Platform, Paint and all other associated works, all in accordance with Specifications. | Item | L.S
1.3 | Allow for testing, cleansing and sterilising of the Tank and Pipework as specified. | Item | L.S
2 | PIPES & FITTINGS
Supply, Transport to Site and Store in Secure Place, Including Jointing Material, Bolts, Gaskets, Packing, Jointing Glue, etc. As applicable
Inlet Pipework - Approved Epoxy Lined Internally and Externally Ferrous Pipe Fittings to Class NP16
2.1 | 150mm dia. flanged ball float valve (Series 1048 Biwater or approved equivalent) (Mark A) | Nr | 1
2.2 | 150mm dia. all flanged pipe, 300mm long with puddle flange at 125mm from one end (Puddle flange welded to tank wall panel) (Mark B) | Nr | 1
2.3 | 150mm dia. all flanged 900 bend (Mark C) | Nr | 2
2.4 | 150mm dia. all flanged pipe 2500mm long (Mark D) | Nr | 1
2.5 | 150mm dia. flanged spigot pipe 12000mm long (cut to suit on site) (Mark E) | Nr | 1
2.6 | 150mm dia. flange adaptor (Mark F) | Nr | 1
2.7 | 150mm dia. flanged spigot pipe 1200mm long (Mark G) | Nr | 1
2.8 | 150mm dia. coupling (Mark H) | Nr | 1
Outlet Pipework - Approved Epoxy Lined Internally and Externally Ferrous Pipes & Fittings to Class NP16
(i) Backwash Water Outlet Pipework
2.9 | 350mm dia. Pipe 1200mm long with one end flanged, bellmouth on the other end and puddle flange at 310mm from the bellmouth (Puddle flange welded to tank base panel) (Mark A) | Nr | 1
2.1 | 350mm dia. flanged spigot pipe 10000mm long (cut to suit on site) (Mark B) | Nr | 1
PAGE TOTAL CARRIED TO BILL COLLECTION PAGE
2.11 | 350mm dia. flange adaptor (Mark C) | Nr | 2
2.12 | 350mm dia. all flanged 900 bend (Mark D) | Nr | 1
2.13 | 350mm dia. all flanged pipe 1,200mm long (Mark E) | Nr | 1
2.14 | 350mm dia. all flanged gate valve (to Euro 20 Series, Type 23 short face to face type valves) as made by PONTA-Mousson (Saint Gobain Pam) or approved equivalent (Mark F) | Nr | 1
2.15 | 350mm dia. Plain ended pipe 2400mm long (cut to suit on site) (Mark G) | Nr | 1
2.16 | 350mm dia. coupling (Mark H) | Nr | 1
(i) Domestic Water Outlet Pipework
2.17 | 80mm dia. Pipe 1200mm long with one end flanged, bellmouth on the other end and puddle flange at 150mm from the bellmouth (Puddle flange welded to tank base panel) (Mark a) | Nr | 1
2.18 | 80mm dia. flanged spigot pipe 10000mm long (Cut to suit on site) (Mark b) | Nr | 1
2.19 | 80mm dia. flange adaptor (Mark c) | Nr | 2
2.2 | 80mm dia. all flanged 900 bend (Mark d) | Nr | 1
2.21 | 80mm dia. all flanged pipe 1,600mm long (Mark e) | Nr | 1
2.22 | 80mm dia. all flanged gate valve (to Euro 20 Series, Type 23 short face to face) as made by PONT-A-Mousson (Saint Gobain Pam) or approved equivalent (Mark f) | Nr | 1
2.23 | 80mm dia. Plain ended pipe 2400mm long (Cut to suit on site) (Mark g) | Nr | 1
2.24 | 80mm dia. coupling (Mark h) | Nr | 1
Overflow Pipework - Approved Epoxy Lined Internally and Externally Ferrous Pipes & Fittings to Class NP16
2.25 | 200mm dia. Flanged spigot pipe, length 300mm with puddle flange 60mm from the spigot end (Puddle flange welded to tank panel (Mark 1) | Nr | 1
2.26 | 200mm dia. all flanged 900 bend (Mark 2) | Nr | 2
2.27 | 200mm dia. all flanged pipe 2500mm long (Mark 3) | Nr | 1
2.28 | 200mm dia. flanged spigot pipe 12m long (cut to suit on site) (Mark 4) | Nr | 1
2.29 | 200mm dia. flange adaptor (Mark 5) | Nr | 1
2.3 | 200mm dia. flanged spigot pipe 1200mm long (Mark 6) | Nr | 1
PAGE TOTAL CARRIED TO BILL COLLECTION PAGE
Scour Pipework - Approved Lined Ferrous Pipes to Class NP16
2.31 | 150mm dia. Flanged bellmouth (welded to base of tank with water tight joint (Mark 7) | Nr | 1
2.32 | 150mm dia. all flanged pipe 1200mm long (Mark 8) | Nr | 1
2.33 | 150mm dia. flanged spigot pipe 10m long (cut to suit on site) (Mark 9) | Nr | 1
2.34 | 150mm dia. flange adaptor (Mark 10) | Nr | 1
2.35 | 150mm dia. all flanged 900 bend (Mark 11) | Nr | 1
2.36 | 150mm dia. flanged spigot pipe 1000mm long (Mark 12) | Nr | 2
2.37 | 150mm dia. coupling (Mark 13) | Nr | 1
2.38 | 150mm dia. all flanged gate valve (to Euro 20 Series, Type 23 short face to face) as made by PONT-A-Mousson (Saint Gobain Pam) or approved equivalent (Mark 14) | Nr | 1
2.39 | 150mm dia. single flanged 900 bend (Mark 15) | Nr | 1
Transport From Site Store, Install, Test and Commission
Inlet Pipework - Approved Lined Ferrous Pipe and Fittings to Class NP16
2.4 | 150mm dia. flanged ball float valve (Series 1048 Biwater or approved equivalent) (Mark A) | Nr | 1
2.41 | 150mm dia. all flanged pipe, 300mm long with puddle flange at 125mm from one end (puddle flange welded to tank wall panel) (Mark B) | Nr | 1
2.42 | 150mm dia. all flanged 900 bend (Mark C) | Nr | 2
2.43 | 150mm dia. all flanged pipe 2500mm long (Mark D) | Nr | 1
2.44 | 150mm dia. flanged spigot pipe 12000mm long (cut to suit on site) (Mark E) | Nr | 1
2.45 | 150mm dia. flange adaptor (Mark F) | Nr | 1
2.46 | 150mm dia. flanged spigot pipe 1200mm long (Mark G) | Nr | 1
2.47 | 150mm dia. coupling (Mark H) | Nr | 1
Outlet Pipework - Approved Lined Ferrous Pipes & Fittings to Class NP16
(i) Backwash Water Outlet Pipework
2.48 | 350mm dia. Pipe 1200mm long with one end flanged, bellmouth on the other end and puddle flange at 310mm from the bellmouth (Puddle flange welded to tank base panel) (Mark A) | Nr | 1
2.49 | 350mm dia. flanged spigot pipe 10000mm long (Cut to suit on site) (Mark B) | Nr | 1
PAGE TOTAL CARRIED TO BILL COLLECTION PAGE
2.5 | 350mm dia. flange adaptor (Mark C) | Nr | 2
2.51 | 350mm dia. all flanged 900 bend (Mark D) | Nr | 1
2.52 | 350mm dia. all flanged pipe 1,200mm long (Mark E) | Nr | 1
2.53 | 350mm dia. all flanged gate valve (to Euro 20 Series, Type 23 short face to face type valves) as made by PONTA-Mousson (Saint Gobain Pam) or approved equivalent (Mark F) | Nr | 1
2.54 | 350mm dia. Plain ended pipe 2400mm long (Cut to suit on site) (Mark G) | Nr | 1
2.55 | 350mm dia. coupling (Mark H) | Nr | 1
(i) Domestic Water Outlet Pipework
2.56 | 80mm dia. Pipe 1200mm long with one end flanged, bellmouth on the other end and puddle flange at 150mm from the bellmouth (Puddle flange welded to tank base panel) (Mark a) | Nr | 1
2.57 | 80mm dia. flanged spigot pipe 10000mm long (Cut to suit on site) (Mark b) | Nr | 1
2.58 | 80mm dia. flange adaptor (Mark c) | Nr | 2
2.59 | 80mm dia. all flanged 900 bend (Mark d) | Nr | 1
2.6 | 80mm dia. all flanged pipe 1,600mm long (Mark e) | Nr | 1
2.61 | 80mm dia. all flanged gate valve (to Euro 20 Series, Type 23 short face to face) as made by PONT-A-Mousson (Saint Gobain Pam) or approved equivalent (Mark f) | Nr | 1
2.62 | 80mm dia. Plain ended pipe 2400mm long (Cut to suit on site) (Mark g) | Nr | 1
2.63 | 80mm dia. coupling (Mark h) | Nr | 1
Overflow Pipework - Approved Lined Ferrous Pipes & Fittings to Class NP16
2.64 | 200mm dia. Flanged spigot pipe, length 300mm with puddle flange 60mm from the spigot end (Puddle flange welded to tank panel (Mark 1) | Nr | 1
2.65 | 200mm dia. all flanged 900 bend (Mark 2) | Nr | 2
2.66 | 200mm dia. all flanged pipe 2500mm long (Mark 3) | Nr | 1
2.67 | 200mm dia. flanged spigot pipe 12m long (cut to suit on site) (Mark 4) | Nr | 1
2.68 | 200mm dia. flange adaptor (Mark 5) | Nr | 1
2.69 | 200mm dia. flanged spigot pipe 1200mm long (Mark 6) | Nr | 1
PAGE TOTAL CARRIED TO BILL COLLECTION PAGE
Scour Pipework - Approved Lined Ferrous Pipes & Fittings to Class NP16
2.7 | 150mm dia. Flanged bellmouth (welded to base of tank with water tight joint (Mark 7) | Nr | 1
2.71 | 150mm dia. all flanged pipe 1200mm long (Mark 8) | Nr | 1
2.72 | 150mm dia. flanged spigot pipe 10m long (cut to suit on site) (Mark 9) | Nr | 1
2.73 | 150mm dia. flange adaptor (Mark 10) | Nr | 1
2.74 | 150mm dia. all flanged 900 bend (Mark 11) | Nr | 1
2.75 | 150mm dia. flanged spigot pipe 1000mm long (Mark 12) | Nr | 2
2.76 | 150mm dia. coupling (Mark 13) | Nr | 1
2.78 | 150mm dia. all flanged gate valve (to Euro 20 Series, Type 23 short face to face) as made by PONT-A-Mousson (Saint Gobain Pam) or approved equivalent (Mark 14) | Nr | 1
2.79 | 150mm dia. single flanged 900 bend (Mark 15) | Nr | 1
3 | CHAMBERS
Note: Items for work in this shall include:-
- Excavation, preparation of surfaces, disposal of excavated material, shoring sides of excavation, backfilling and removal of redundant services.
- Concrete, Reinforcement, Formwork, Joints, Finishes, Benching, etc.
=- Tips for disposal of excavated material or debris to be identified by the Contractor in liaison with the Local Authority.
Concrete Chambers
Depth not exceeding 2.0m
3.1 | Provide all materials and construct Valve Chambers Internal Dimensions 2400mm x 2000mm depth not exceeding 2.0m. Include for supply and fixing of lockable mild steel checkered plate cover & step irons | Nr | 1
3.2 | -Ditto- but chambers internal dimension 1500 x 1500mm, depth n.e 2.0m | Nr | 1
4 | REINFORCED CONCRETE FOUNDATIONS
4.1 | Excavation
The rates shall include for all strutting, shuttering, stabilising the excavation faces, and keeping the excavation free of water by pumping, bailing or other means.
Excavate in common material, part backfill after construction and remainder, cart away to tips or use as fill on site, all as directed by the Engineer.
4.1.1 | Maximum depth n.e. 1.0 m | m3 | 35
PAGE TOTAL CARRIED TO BILL COLLECTION PAGE
4.1.2 | -Ditto- but maximum depth 1.0 m to 2.0 m | m3 | 25
4.1.3 | Extra over Items 4.1.1 to 4.1.2 for excavation in rock Class 'A', blasting not permitted (Provisional) | m3 | 6
4.1.4 | -Ditto- for excavation in rock Class 'B' (Provisional) | m3 | 9
4.1.5 | -Ditto- for excavation in rock Class 'C' (Provisional) | m3 | 4
4.2 | Concrete Works
Provide, mix and place concrete as directed
4.2.1 | Plain concrete Class 15/20 in 75mm blinding layer under base slab of tank | m2 | 32
Guaranteed Strength Reinforced Concrete Class 25/20. Maximum Aggregate as Described in:-
4.2.2 | Column Base Slab | m3 | 16
4.2.3 | Columns | m3 | 4
4.3 | Reinforcement
Provide and Fix High Tensile Steel Reinforcement to SRN 127 including Cutting, Bending, Propping with Spacers and Tying as Specified:-
4.3.1 | Reinforcement, all diameters | Kg | 2400
4.4 | Formwork
Provide and Fix Shuttering including Propping, Strutting and Striking all as Specified
(i) Vertical Formwork - Class F1 Finish
4.4.1 | Sides of 500 mm Column Base Slab - Tank | m2 | 24
4.4.2 | Sides of Columns | m2 | 18
PAGE TOTAL CARRIED TO BILL COLLECTION PAGE
Note on A45: Mohamed Ibrahim:

## Collection Sheet 3.9
TETU-AGUTHI WATER SUPPLY PROJECT
BILL No. 3.9
ELEVATED BACKWASH WATER TANK (150m³ )
Amount
Kshs.
Page Total, Page 1 of 6
Page Total, Page 2 of 6
Page Total, Page 3 of 6
Page Total, Page 4 of 6
Page Total, Page 5 of 6
Page Total, Page 6 of 6
Bill No. 3.7 Total Exclusive of VAT Carried to Section 3 Summary Sheet

## Sludge lagoon
TETU-AGUTHI WATER SUPPLY PROJECT
BILL No. 3.10
BACKWASH WATER AND SLUDGE LAGOON AND RECIRCULATION PUMP CHAMBER
ITEM | DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
No. |  |  |  | (Kshs) | (Kshs)
1 | EXCAVATION
The rates shall include for all strutting, shuttering, stabilising the excavation faces, and keeping the excavation free of water by pumping, bailing or other means.
Bulk excavations and top soil stripping for all structures are measured under Bill No. 3.11 (Site & Ancillary Works).
Excavate for foundations, part backfill after construction and remainder, cart away to tips or use as fill on site, all as directed by the Engineer
Excavate below stripped level to formation level in common material, part backfill after construction and remainder, cart away to tips or use as fill on site, all as directed by the Engineer.
Quantites are combined for Recirculation Pump Chamber, Backwash water and Sludge Lagoon
1.1 | Maximum depth n.e. 1.0 m | m3 | 687
1.2 | -Ditto- but maximum depth 1.0 m to 2.0 m | m3 | 515
1.3 | -Ditto- but maximum depth 2.0 m to 3.0 m | m3 | 66
1.4 | Extra over excavation for partitioning wall base | m3 | 23
1.5 | Preparation of excavated surfaces including trimming sides of excavation to 34 degrees slope | m2 | 246
1.6 | Extra Over Item 1.1 to 1.4 for excavation in rock Class 'A', Blasting not permitted (Provisional) | m3 | 78
1.7 | Extra Over Item 1.1 to 1.4 for excavation in rock Class 'B', Blasting not permitted (Provisional) | m3 | 130
1.8 | Extra Over Item 1.1 to 1.4 for excavation in rock Class 'C', Blasting not permitted (Provisional) | m3 | 52
Fill
Transport approved excavated material from site and use as fill and compact in 200 mm layers as specified on site as and where directed by the Engineer. Compaction tests to be done and rates to include for this
1.9 | Fill to Finished Ground Level around the Sludge and Backwash water Lagoons, Inlet and Scour Chambers and Recirculation pump chamber. | m3 | 156
1.10 | Under concrete access ramp | m3 | 18
1.11 | Cart away surplus excavated materials to an approved dumping site | m3 | 1117
PAGE TOTAL CARRIED TO SECTION COLLECTION SHEET
2 | CONCRETE WORKS
Provide, mix and place concrete as directed:
2.1 | Plain concrete class 15/20 in 75mm thick blinding under the base of Backwash Water Lagoon, Sludge Lagoon and RC partition wall | m3 | 12
2.2 | -Ditto- on sides of Backwash Water Lagoon and Sludge Lagoon at 45 degrees slope including all necessary formwork | m3 | 18
2.3 | -Ditto- under the base slab of Inlet and Scour Chambers | m3 | 1
2.4 | -Ditto- under the Recirculation Chamber base slab | m3 | 3
Vibrated reinforced concrete class 25/20 in:
2.5 | 100mm thick Base Slab of Backwash Water Lagoon and Sludge Lagoon | m3 | 16
2.6 | -Ditto- on sides of Backwash Water Lagoon and Sludge Lagoon at 45 degrees slope including all necessary formwork | m3 | 24
2.7 | 175mm thick Top Sorround Slab of Backwash Water Lagoon and Sludge Lagoon | m3 | 4
2.8 | 200mm thick Base Slab of Inlet and Scour Chambers | m3 | 9
2.9 | -Ditto- base of Recirculation Pump Chamber | m3 | 3
2.10 | -Ditto- slab on top surface of access ramp at slope n.e. 15 degrees, including all necessary formwork | m3 | 6
2.11 | -Ditto- walls retaining fill under ramp | m3 | 4
2.12 | Extra over item 2.7 above for forming ribbed surface finish on concrete slab on access ramp | m2 | 29
2.13 | 200mm thick Base Slab of RC Lagoon partition wall | m3 | 6
2.14 | -Ditto- Roof slab of Recirculation Pump Chamber | m3 | 2
2.15 | -Ditto- walls of Scour Chambers | m3 | 23
2.16 | -Ditto- walls of Recirculation Pump Chamber | m3 | 8
2.17 | 75mm thick Precast Concrete Cover Slab of Recirculation Pump Chamber, size 2300mm long x 400mm wide x 200mm thick in two equal parts wide including 4 Nr. mild steel key holes cast with slab constructed. | Nr | 2
3 | REINFORCEMENT
Provide and fix high tensile reinforcement to SRN 127, including cutting, bending, propping with spacers and tying as specified
3.1 | Reinforcement, all diameters | kg | 7800
3.2 | Mesh reinforcement type A393 weighing 6.16 kg/m2 on backwash water lagoon and sludge lagoon base slab and sloping surfaces | m2 | 487
PAGE TOTAL CARRIED TO SECTION COLLECTION SHEET
4 | FORMWORK
Provide and fix shuttering including propping, strutting and striking, all as specified
Vertical Formwork - Class F1 Finish
4.1 | Sides of base slab of Backwash Water Lagoon and Sludge Lagoon, width n.e 0.2m | m2 | 10
4.2 | -Ditto- for base slab RC Lagoon partition wall | m2 | 9
4.3 | -Ditto- for base slab of Scour Chambers | m2 | 13
4.4 | -Ditto- for base slab of Recirculation Pump Chamber | m2 | 4
Vertical Formwork - Class F3 Finish
4.5 | 175mm thick Top Sorround Slab of Backwash Water Lagoon and Sludge Lagoon | m2 | 32
4.6 | Sides of RC Lagoon partition wall width n.e 3.0m | m2 | 101
4.7 | -Ditto- walls of Scour Chambers | m2 | 128
4.8 | -Ditto- walls of Recirculation Pump Chamber | m2 | 75
4.9 | -Ditto- Roof slab of Recirculation Pump Chamber | m2 | 4
4.10 | Sides of the wall retaining fill under the Ramp | m2 | 18
Sloping Formwork - Class F3 Finish
4.11 | Sides of Backwash Water Lagoon and Sludge Lagoon at 34 degrees slope | m2 | 234
4.12 | Sides of 200mm thick slab on top surface of access ramp at slope n.e. 9 degrees | m2 | 6
Other Formwork - Class F3 Finish
4.13 | Boxing out 500mm x 500mm holes in concrete walls of Backwash Water Lagoon and Sludge Scour Chamber and making good after installation of pipework | Nr | 3
4.14 | Boxing out 350mm x 350mm holes in concrete walls of Backwash Water Lagoon and Sludge Lagoon and their inlet and outlet chambers. Rate includes making good after installation of pipework. | Nr | 6
4.15 | Boxing out 250mm x 250mm holes in concrete walls of Backwash Water Lagoon and Sludge Lagoon; their inlet and outlet chambers and the Recirculation Pump Chamber. Rate includes making good after installation of pipework | Nr | 12
5 | CONCRETE SURFACE FINISHES
Granolithic Concrete
5.1 | Provide all materials and lay grano-finish 75mm thick to slopes and bases of Backwash Water Lagoon and Sludge Lagoon. | m2 | 490
PAGE TOTAL CARRIED TO SECTION COLLECTION SHEET
6 | PIPEWORK
APPROVED LINED FERROUS PIPES TO PN 16
Supply, transport to site and store in secure place, including jointing materials, bolts, gaskets, packing, jointing glues, etc. as applicable
Backwash Water Lagoon Supernatant Draw-Off And Overflow Pipework.
6.1 | 250mm dia. Single Flanged 90° Bend (Mark a) | Nr | 3
6.2 | 250mm dia. All Flanged Gate Valve with extended spindle and wheel (Mark b) | Nr | 3
6.3 | 250mm dia. Flanged Spigot Pipe, length 2.4m with puddle flange at 750mm from flanged end and with spigot end bevelled (cut to suit on site) (Mark c1) | Nr | 1
6.4 | -Ditto- length 2.95m (Mark c2) | Nr | 1
6.5 | -Ditto- length 3.6m (Mark c3) | Nr | 1
6.6 | 300mm dia. Flanged Spigot Pipe, length 1.75m with puddle flange at 750mm from flanged end and with spigot end bevelled (cut to suit on site) (Mark d) | Nr | 1
6.7 | 300mm dia. Single Flanged 90° Bend (Mark e) | Nr | 1
Sludge Lagoon Supernatant Draw-Off And Overflow Pipework
6.8 | 200mm dia. Single Flanged 90° Bend (Mark A) | Nr | 3
6.9 | 200mm dia. All Flanged Gate Valve with extended spindle and wheel (Mark B) | Nr | 3
6.1 | 200mm dia. Flanged Spigot Pipe, length 2.85m with puddle flange at 565mm from flanged end and with spigot end bevelled (cut to suit on site) (Mark C1) | Nr | 1
6.11 | -Ditto- length 3.45m (Mark C2) | Nr | 1
6.12 | -Ditto- length 4.1m (Mark C3) | Nr | 1
6.13 | 250mm dia. Flanged Spigot Pipe, length 2.35m with puddle flange at 565mm from flanged end and with spigot end bevelled (cut to suit on site) (Mark D) | Nr | 1
6.14 | 250mm dia. Single Flanged 90° Bend (Mark E) | Nr | 1
Recirculation Pipework
Delivery Pipework to Stilling Well
6.15 | 100mm dia Flanged Spigot Pipe 400mm long (Cut to suit on site) (Mark 1) | Nr | 2
PAGE TOTAL CARRIED TO SECTION COLLECTION SHEET
6.16 | 100mm dia All Flanged 90° Bend (Mark 2) | Nr | 5
6.17 | 100mm dia Flange Adaptor (Mark 3) | Nr | 4
6.18 | 100mm dia Flanged Spigot Pipe 1200mm long (Cut to suit on site) (Mark 4) | Nr | 2
6.19 | 100mm dia All Flanged Pipe 600mm long with puddle flange at 300mm from one end. (Mark 5) | Nr | 3
6.2 | 100mm dia Double Flanged free-acting Check Valve (Non-return valve) (Mark 6) | Nr | 2
6.21 | 100mm dia All flanged Gate Valve with 2400mm long extension spindle and T-key (Mark 7) | Nr | 2
6.22 | 100mm dia Flanged Spigot Pipe, 685mm long (Mark 8) | Nr | 2
6.23 | 100×100×100 mm dia All Flanged Tee (Mark 9) | Nr | 1
6.24 | 100×150 mm dia All Flanged Concentric Taper (Mark 10) | Nr | 1
6.25 | 150mm dia Flanged Spigot Pipe, 1200mm long (Mark 11) | Nr | 1
6.26 | 150mm dia Coupling (Mark 12) | Nr | 1
Overflow and Scour Pipework
6.27 | 150mm dia.Flanged Spigot 900 bend with puddle flange at 100mm from spigot end (Mark i) | Nr | 1
6.28 | 150mm dia. Flanged pipe 800mm long (Cut to Suit on site) (Mark ii) | Nr | 1
6.29 | 150mm Dia flanged 4500 bend (Mark iii) | Nr | 1
6.30 | 150mm dia Flanged spigot pipe 920mm long with the Spigot end bevelled (Cut to suit on site) (Mark iv) | Nr | 1
6.31 | 150mm dia flanged spigot pipe 1085mm long with puddle flange at 100 mm from the spigot end (Mark v) | Nr | 1
6.32 | 150mm dia Flanged Gate Valve with extended spindle 3000mm long (Mark vi) | Nr | 1
CONCRETE S&S PIPES
Backwash Water Lagoon Pipework
6.33 | Backwash Water Lagoon inlet pipe; 450mm dia Concrete socket and spigot pipe 1.2m long with one end bevelled (Cut to suit on Site) | Nr | 1
6.34 | Backwash Water Lagoon Outlet Chamber outlet pipe; 300 mm dia Concrete socket and Spigot pipe 600mm long (Cut to suit on site) | Nr | 1
PAGE TOTAL CARRIED TO SECTION COLLECTION SHEET
Sludge Lagoon Pipework
6.35 | Sludge lagoon inlet pipe; 225mm dia Concrete socket and spigot pipe 1.2m long with one end bevelled (Cut to suit on Site) | Nr | 1
6.36 | Sludge Lagoon Outlet Chamber outlet pipe; 225 mm dia Concrete socket and Spigot pipe 10.6 m long (Cut to suit on site) | Nr | 1
Transport from Site Store, Install,Test and Commission
APPROVED LINED FERROUS PIPES TO PN 16
Backwash Water Lagoon Supernatant Draw-Off And Overflow Pipework
6.37 | 250mm dia. Single Flanged 90° Bend (Mark a) | Nr | 3
6.38 | 250mm dia. All Flanged Gate Valve with extended spindle and wheel (Mark b) | Nr | 3
6.39 | 250mm dia. Flanged Spigot Pipe, length 2.4m with puddle flange at 750mm from flanged end and with spigot end bevelled (cut to suit on site) (Mark c1) | Nr | 1
6.40 | -Ditto- length 2.95m (Mark c2) | Nr | 1
6.41 | -Ditto- length 3.6m (Mark c3) | Nr | 1
6.42 | 300mm dia. Flanged Spigot Pipe, length 1.75m with puddle flange at 750mm from flanged end and with spigot end bevelled (cut to suit on site) (Mark d) | Nr | 1
6.43 | 300mm dia. Single Flanged 90° Bend (Mark e) | Nr | 1
Sludge Lagoon Supernatant Draw-Off And Overflow Pipework
6.44 | 200mm dia. Single Flanged 90° Bend (Mark A) | Nr | 3
6.45 | 200mm dia. All Flanged Gate Valve with extended spindle and wheel (Mark B) | Nr | 3
6.46 | 200mm dia. Flanged Spigot Pipe, length 2.85m with puddle flange at 565mm from flanged end and with spigot end bevelled (cut to suit on site) (Mark C1) | Nr | 1
6.47 | -Ditto- length 3.45m (Mark C2) | Nr | 1
6.48 | -Ditto- length 4.1m (Mark C3) | Nr | 1
6.49 | 250mm dia. Flanged Spigot Pipe, length 2.35m with puddle flange at 565mm from flanged end and with spigot end bevelled (cut to suit on site) (Mark D) | Nr | 1
6.50 | 250mm dia. Single Flanged 90° Bend (Mark E) | Nr | 1
PAGE TOTAL CARRIED TO SECTION COLLECTION SHEET
Recirculation Pipework
Delivery Pipework to Stilling Well
6.51 | 100mm dia Flanged Spigot Pipe 400mm long (Cut to suit on site) (Mark 1) | Nr | 2
6.52 | 100mm dia All Flanged 90° Bend (Mark 2) | Nr | 5
6.53 | 100mm dia Flange Adaptor (Mark 3) | Nr | 4
6.54 | 100mm dia Flanged Spigot Pipe 1200mm long (Cut to suit on site) (Mark 4) | Nr | 2
6.55 | 100mm dia All Flanged Pipe 600mm long with puddle flange at 300mm from one end. (Mark 5) | Nr | 3
6.56 | 100mm dia Double Flanged free-acting Check Valve (Non-return valve) (Mark 6) | Nr | 2
6.57 | 100mm dia All flanged Gate Valve with 2400mm long extension spindle and T-key (Mark 7) | Nr | 2
6.58 | 100mm dia Flanged Spigot Pipe, 685mm long (Mark 8) | Nr | 2
6.59 | 100×100×100 mm dia All Flanged Tee (Mark 9) | Nr | 1
6.60 | 100×150 mm dia All Flanged Concentric Taper (Mark 10) | Nr | 1
6.61 | 150mm dia Flanged Spigot Pipe, 1200mm long (Mark 11) | Nr | 1
6.62 | 150mm dia Coupling (Mark 12) | Nr | 1
Overflow and Scour Pipework
6.63 | 150mm dia.Flanged Spigot 900 bend with puddle flange at 100mm from spigot end (Mark i) | Nr | 1
6.64 | 150mm dia. Flanged pipe 800mm long (Cut to Suit on site) (Mark ii) | Nr | 1
6.65 | 150mm Dia flanged 4500 bend (Mark iii) | Nr | 1
6.66 | 150mm dia Flanged spigot pipe 920mm long with the Spigot end bevelled (Cut to suit on site) (Mark iv) | Nr | 1
6.67 | 150mm dia flanged spigot pipe 1085mm long with puddle flange at 100 mm from the spigot end (Mark v) | Nr | 1
6.68 | 150mm dia Flanged Gate Valve with extended spindle 3000mm long (Mark vi) | Nr | 1
PAGE TOTAL CARRIED TO SECTION COLLECTION SHEET
CONCRETE S&S PIPES
Backwash Water Lagoon Pipework
6.69 | Backwash Water Lagoon inlet pipe; 450mm dia Concrete socket and spigot pipe 1.2m long with one end bevelled (Cut to suit on Site) | Nr | 1
6.70 | Backwash Water Lagoon Outlet Chamber outlet pipe; 300 mm dia Concrete socket and Spigot pipe 600mm long (Cut to suit on site) | Nr | 1
Sludge Lagoon Pipework
6.71 | Sludge lagoon inlet pipe; 225mm dia Concrete socket and spigot pipe 1.2m long with one end bevelled (Cut to suit on Site) | Nr | 1
6.72 | Sludge Lagoon Outlet Chamber outlet pipe; 225 mm dia Concrete socket and Spigot pipe 10.6 m long (Cut to suit on site) | Nr | 1
7 | PUMPS
Recirculation Pumps
7.1 | Supply, transport to site, install, test and commission submersible pumps (1 duty, 1 standby) complete with motor, base plate, fixing bolts, grouting, etc., for the following characteristics: Flow 68m3 per hour, dynamic head 18m, KSB Amarex 80-251 or approved. equivalent | Nr | 2
8 | METALWORK
8.1 | Provide and fix lockable G.M.S Open Mesh Flooring to sludge lagoon inlet chamber 800mm x 800mm | Nr | 1
8.2 | Ditto but for- Sludge Lagoon Outlet Chamber 3100mm x 1800mm | Nr | 1
8.3 | Ditto but for- Backwash Water Lagoon Inlet Chamber 1200mm x 1200mm | Nr | 1
8.4 | Ditto but for- Backwash Water Lagoon Outlet Chamber 4050mm x 2200mm | Nr | 1
8.5 | Ditto but for- Sludge Scour Chamber 2200mm x 1800mm | Nr | 1
8.6 | Ditto but for- Recirculation Pump Chamber 2500mm x 1000mm | Nr | 1
8.7 | Ditto but for Recirculation Pump Chamber Scour chamber 1500mmx1500mm | Nr | 1
8.8 | Provide and fix step irons at 300mm c/c in the Recirculation Pump Chamber | Nr | 8
8.9 | Ditto- but for Sludge Lagoon outlet chamber | Nr | 8
8.10 | Ditto- but for Backwash Water lagoon outlet chamber | Nr | 8
8.11 | Ditto- but for recirculation pump chamber Scour and Overflow chamber | Nr | 10
8.12 | Ditto- but for Sludge Scour chamber | Nr | 7
8.13 | Ditto- but for Pump Control chamber | Nr | 4
PAGE TOTAL CARRIED TO SECTION COLLECTION SHEET

## Collection Sheet 3.10
TETU-AGUTHI WATER SUPPLY PROJECT
BILL No. 3.10
PAGE TOTALS COLLECTION SHEET
Amount
Kshs.
Page Total, Page 1 of 8
Page Total, Page 2 of 8
Page Total, Page 3 of 8
Page Total, Page 4 of 8
Page Total, Page 5 of 8
Page Total, Page 6 of 8
Page Total, Page 7 of 8
Page Total, Page 8 of 8
Bill No. 3.8 Total Exclusive of VAT Carried to Section 3 Summary Sheet

## Sludge drying beds
TETU-AGUTHI WATER SUPPLY PROJECT
BILL No. 3.11
TREATMENT WORKS - SLUDGE DRYING BEDS
ITEM | DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
No. |  |  |  | (Kshs) | (Kshs)
1 | EXCAVATION
The rates shall include for all strutting, shuttering, stabilising the excavation faces, and keeping the excavation free of water by pumping, bailing or other means
Excavate to formation level in common material, part backfill after construction and reminder, cart away to tips identified by the Contractor in liaison with Local Authorities or use as fill on site, all as directed by the Engineer
1.1.1 | Maximum depth n.e. 1.0m | m3 | 130
1.1.2 | -Ditto- but maximum depth 1.0m to 2.0m | m3 | 70
1.1.3 | -Ditto- but maximum depth 2.0m to 3.0m | m3 | 10
1.1.4 | Provide and place approved hardcore packing, hand packed and compacted to Engineer's approval, maximum 300mm thick layer. Rate to include for provision, packing and compaction. | m3 | 65
1.1.5 | Extra Over Items 1.1 to 1.5 for excavation in rock Class 'A', Blasting not permitted (Provisional) | m3 | 15
1.1.6 | Extra Over Items 1.1 to 1.5 for excavation in rock Class 'B', Blasting not permitted (Provisional) | m3 | 25
1.1.7 | Extra Over Items 1.1 to 1.5 for excavation in rock Class 'C', Blasting not permitted (Provisional) | m3 | 10
1.2 | FILL
1.2.1 | Transport approved excavated material from site stock pile and use as fill. Compact in 200mm thick layers,making up levels under the sludge drying bed base slab as directed by the Engineer. Compaction tests to be done for each layer as directed by the Engineer and to be included in the contractor's rates. | m3 | 50
1.2.2 | Provide, lay and level out the crushed stone, sand or gravel blinding 50mm thick to surface of filling, including watering and rolling to achieve satisfactory compaction. | m2 | 70
1.13 | Trim sides of excavation to 60 degree slopes | m2 | 190
2 | CONCRETE WORKS
Provide, mix and place concrete as directed
2.1 | Plain Concrete Class 15/20 in 50mm thick blinding layer under walls, bases of Sludge Dying Beds and Bases of Sludge Loading Bays. | m2 | 250
PAGE TOTAL CARRIED TO COLLECTION PAGE
Guaranteed Strength Reinforced Concrete Class 25/20. Maximum Aggregate as Described in:-
2.2 | Base Slab - Drainage channel | m3 | 6
2.3 | Base Slab - Beds- 300mm thick | m3 | 58
2.4 | Base Slab - Sludge Loading Bays - 200mm thick | m3 | 4
2.5 | Base Slab - Sludge Distribution Channel - 200mm thick | m3 | 4
2.6 | Base Slab - Outlet Chambers - 300mm thick | m3 | 2
2.7 | Base Slab - Inlet Chambers - 200mm thick | m3 | 2
2.8 | Walls - Drainage Channel - 300mm thick | m3 | 7
2.9 | Walls - Sludge Drying Beds - 300mm thick | m3 | 56
2.1 | Walls - Sludge Distribution Channel - 125mm thick | m3 | 2
2.11 | Walls - Outlet Chambers - 200mm thick | m3 | 4
2.12 | Walls - Inlet Chambers - 200mm thick | m3 | 3
2.13 | Columns - 400mm x 200mm | m3 | 1
2.14 | Roof Slab - Outlet Chamber, 150 mm thick | m² | 2
3 | REINFORCEMENT
Provide and Fix High Tensile Steel Reinforcement to SRN 127 including Cutting, Bending, Propping with Spacers and Tying as Specified:-
3.1 | High Yield Reinforcement Bars, all diameters | Kg | 17280
4 | FORMWORK
Provide and Fix Shuttering Including Propping, Strutting and Striking, all as specified
(i) Vertical Formwork - Class F1 Finish
4.1 | Sides of Slabs - width n.e 0.3m | m | 96
4.2 | Sides of Walls - width ne. 3.5m | m2 | 156
(ii) Vertical Formwork - Class F3 Finish
4.3 | Sides of Walls - width ne. 0.1m | m | 81
4.4 | Sides of Walls - width n.e 3.5m | m2 | 210
4.5 | Sides of Walls Sludge Distribution Channel - width n.e. 0.3m | m | 95
PAGE TOTAL CARRIED TO COLLECTION PAGE
4.6 | Sides of Base Sludge Distribution Channel - width n.e. 0.2m | m | 48
4.7 | Sides of Columns - width n.e 0.2m | m | 15
4.8 | Sides of Columns - width n.e 0.4m | m | 15
4.9 | Soffits of Sludge Distribution Channel - width n.e. 0.65m | m2 | 16
4.1 | Sides of Concrete roof slab for Outlet Chamber - width n.e 0.15m | m | 6
Other Formwork
4.11 | Box out for 400mm dia. pipes in 200mm thick Concrete Walls of Inlet Chambers and make good after Installation of Sludge Inlet Pipes. | Nr | 3
4.12 | Box out for 225mm dia. pipes in 200mm thick Concrete Walls of Outlet Chambers and make good after Installation of the Outlet Pipes. | Nr | 1
4.13 | Boxing out 400 mm x 400 mm holes in 300mm thick concrete walls and making good for sludge inlet pipes | Nr | 2
5 | WALLING
Selected Machine Dressed Natural Stone Block Walling, Reinforced with 20 swg Hoop Iron at every alternate course, and Bedded, Jointed and Pointed in Cement Mortar (1:3):-
5.1 | 200mm Thick Walling | m² | 20
6 | PRECAST CONCRETE
6.1 | Precast concrete slabs class 25/20 finished fair on all surfaces, size 400mm x 600mm x 75mm thick, laid on surface of filter media as per details on Drg. No. M407/CG/TW/NJ/SDB/02. | Nr | 750
7 | CONSTRUCTION JOINTS
Provide and install the following waterstops in construction joints including all surface treatment, formwork, forming of rebate 20 mm x 20 mm and sealing of rebate with polysulphide sealant all as per Drawings and Specification
7.1 | 200 mm wide expandite super-cast waterfoil PVC or similar approved waterstop in vertical/horizontal construction joints in walls | m | 70
8 | PIPEWORK, FITTINGS AND VALVES
Supply, transport to site and store in secure place, including jointing material, bolts gaskets, packing, jointing glues, etc. as applicable
Drainage Channel Pipework
8.1 | 225mm dia. open jointed perforated concrete pipe 17m long | Nr | 1
PAGE TOTAL CARRIED TO COLLECTION PAGE
Inlet Manhole Pipework
8.2 | 400mm dia. concrete socket and spigot pipe, 1200mm long (cut to suit on site) | Nr | 6
Transport from Site Store, Install, Test and Commission. This rate includes provisions for all jointing and fixing materials
8.3 | 225mm dia. open jointed perforated concrete pipe 17m long | Nr | 1
8.4 | 400mm dia. concrete socket and spigot pipe (cut to suit on site) | m | 7
9 | METAL WORK
All Steel Works to be completely cleaned by acid dipping prior to galvanising
9.1 | G.M.S Hand Stops at Inlet Chamber | Nr | 5
10 | MISCELLANEOUS
10.1 | Provide and Place approved Filter Medium of Clean Sharp Sand 6mm nominal size in Drying Bed and finish level | m3 | 54
10.2 | - Ditto - but gravel, 19mm | m3 | 27
10.3 | - Ditto - but large stones, 38mm | m3 | 27
PAGE TOTAL CARRIED TO COLLECTION PAGE

## Collection Sheet 3.11
TETU-AGUTHI WATER SUPPLY PROJECT
BILL No. 3.11
PAGE TOTALS COLLECTION SHEET
Amount
Kshs.
Page Total, Page 1 of 4
Page Total, Page 2 of 4
Page Total, Page 3 of 4
Page Total, Page 4 of 4
Bill No. 3.9 Total Exclusive of VAT Carried to Section 3 Summary Sheet

## Admin Building
TETU-AGUTHI WATER SUPPLY PROJECT
BILL No. 3.12
TREATMENT WORKS ADMINISTRATION BUILDING
ITEM | DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
No. |  |  |  | Kshs | KShs.
1 | SUBSTRUCTURES (PROVISIONAL)
Site clearance and top soil stripping for all structures measured under Bill No. 2/3.9 - Site and Ancillary Works.
Excavations and Earthworks
1.1 | Stack excavated vegetable top soil on site for re-use | m3 | 29
Excavate 0.00 - 1.50m deep starting from stripped levels to receive :-
1.2 | Strip foundations | m3 | 62
Extra over excavation in any position for:-
1.3 | Excavating in compacted gravel or decomposed rock | m3 | 3
1.4 | Excavating in coral or hard material | m3 | 3
Stack excavated material on site:-
1.5 | Stack excavated material arising from excavation on site for re-use | m3 | 91
Approved Filling from stacked materials
1.6 | Remove from stack and fill and ram materials around foundation trenches and column bases | m3 | 27
Disposal
1.7 | Load and cart away excess excavated soil to an approved dumping site | m3 | 64
Approved filling as described:-
1.8 | Provide and deposit approved hardcore fill material 225mm thick in maximum 100mm thick layers in making up levels | m2 | 78
1.9 | Provide, lay and level out, 50mm thick murram or quarry chips blinding to surface of filling, including watering and rolling to achieve satisfactory compaction | m2 | 78
1.1 | Hand packing hardcore to form vertical or battering face 100mm wide | m | 3
Anti-Termite Treatment
1.11 | Chemical anti-termite treatment to surface of filling with an approved insecticide | m2 | 147
Damp-proof Membrane
1.12 | 500 Gauge polythene damp-proof membrane laid in 2 layers, laid over blinding | m2 | 95
PAGE TOTAL CARRIED TO BILL COLLECTION PAGE
CONCRETE
Mass Concrete Class P 15/20mm, maximum aggregate as described in:-
1.13 | 50mm Thick blinding under foundation concrete | m3 | 5
Guaranteed Strength Reinforced Concrete Class 25/20mm maximum aggregate as described in:-
1.14 | Strip foundations | m3 | 11
1.15 | Column bases and foundation columns | m3 | 2
1.16 | 150mm Thick floor slab | m3 | 15
Reinforcement ( All Provisional)
1.17 | Fabric Reinforcement No. A142 Mesh Size 150 x 150mm Weighing 2.22 kgs Per m2 , with minimum 150mm wide side and end laps, laid in bed. | m2 | 95
Hot Rolled High Yield Steel Deformed Bars to B.S.4449, Including Bends, Hooks, Tying wire, Distance Blocks and Ordinary Spacers:-
1.18 | 10mm Diameter | Kg | 390
1.19 | 12mm Diameter | Kg | 390
1.2 | 16mm Diameter | Kg | 390
1.21 | 20mm Diameter | Kg | 390
Formwork
Formwork to surfaces, including cutting fins or filling of small voids
1.22 | Vertical sides of column | m2 | 20
1.23 | Edges of surface bed 150mm high | m | 48
Walling
Natural Coral Stone Walling, Medium Chisel Dressed, Reinforced with 20 swg Hoop Iron at every alternate course, and Bedded, Jointed and Pointed in Cement Mortar (1:3):-
1.24 | 200 mm Walling | m2 | 99
PAGE TOTAL CARRIED TO BILL COLLECTION PAGE
Damp-proof course:
One layer bitumen felt damp proof course to B.S. 743, Type A, Hessian base, weighing 3.8 kgs. per m2 with 150mm laps, bedded in cement mortar
1.25 | 100mm Wide under walls | m | 1
1.26 | 200mm Wide under walls | m | 64
Plinths
1.27 | 15mm Cement and sand (1:4) render to plinth walls, finished with a wood float | m2 | 17
1.28 | Prepare and apply two coats of bituminous paint on rendered plinth walls | m2 | 17
Allow for the Following :-
1.29 | Allow for keeping the whole of the excavations free from all spring and running water by pumping or other such means as may be necessary | Item | L.S
1.3 | Allow for maintaining and upholding the sides of excavations clear of all fallen materials, rubbish etc. | Item | L.S
2 | SUPERSTRUCTURE
CONCRETE WORK
Guaranteed Strength Reinforced Concrete Class 25/20mm maximum aggregate as described in:-
2.1 | Columns | m3 | 3
2.2 | Beams | m3 | 5
Reinforcement
Hot Rolled High Yield Steel Deformed Bars to B.S.4449, Including Bends, Hooks, Tying wire, Distance Blocks and Ordinary Spacers:-
2.3 | 8mm Diameter | Kg | 192
2.4 | 10mm Diameter | Kg | 192
2.5 | 12mm Diameter | Kg | 192
2.6 | 16mm Diameter | Kg | 192
2.7 | 20mm Diameter | Kg | 192
PAGE TOTAL CARRIED TO BILL COLLECTION PAGE
Formwork
Formwork to surfaces, including cutting fins or filling of small voids
2.8 | Vertical sides of columns | m2 | 40
2.9 | Vertical sides and soffites of horizontal floor or roof beams | m2 | 66
3 | WALLING
External Walls
Selected Coral Stone Block Walling, Fine Chisel Dressed or Machine Dressed, Reinforced with 20 swg Hoop Iron at every alternate courses, and Bedded, Jointed and Pointed in Cement Mortar (1:3):-
3.1 | 200mm Thick walling | m2 | 87
Labours
3.2 | Extra over walling for ruled horizontal joints | m2 | 87
3.3 | Fair raking cutting for walling | m | 11
Precast Concrete Cills
150mm Wide concrete cill bedded, jointed and pointed in cement mortar on top of 200mm wall, and set in window opening :-
3.4 | 600mm Long | Nr | 3
3.5 | 1200mm Long | Nr | 2
3.6 | 1800mm Long | Nr | 5
Internal Walls
Selected Coral Stone Block Walling, Medium Chisel Dressed, Reinforced with 20 swg Hoop Iron at every alternate courses, and Bedded, Jointed and Pointed in Cement Mortar (1:3):-
3.7 | 100mm Thick walling | m2 | 50
3.8 | 200mm Thick | m2 | 4
PAGE TOTAL CARRIED TO BILL COLLECTION PAGE
4 | CARPENTRY AND JOINERY
CARPENTRY
Roof Trusses
Double Pitch Roof Truss With 600mm eaves projection, in 150 x 50mm Rafters, Ceiling Joists, Struts and Ties in Sawn Cypress Grade II Seasoned and Pressure Impregnated with Wood Preservative and timber joints with bolted and nailed connections to the Engineer's approval :-
4.1 | Equal truss 4900mm clear span and 1225mm high | Nr | 10
Other Roof Members
Sawn Cypress Grade II Maximum Moisture Content 12% Seasoned and Pressure Impregnated with Wood Preservative and timber joints with bolted and nailed connections to the Engineer's approval:-
4.2 | 150 x 50mm Intermediate rafters | m | 172
4.3 | 150 x 50mm Purlins | m | 123
4.4 | 200 x 40mm Fascia board | m | 41
4.5 | 200 x 50mm Ridge board | m | 13
4.6 | 100 x 50mm Wall plate tied to wall with 20 s.w.g. hoop iron at 900mm centres | m | 39
4.7 | 40 x 40mm Battens at 300mm centres to receive tiles | m | 260
Sundries
4.8 | Bed wall plate in cement mortar (1:4) | m | 39
5 | EXTERNAL AND INTERNAL OPENINGS
DOORS, FRAMES, ETC
Timber Door Frames
Wrot Cypress
Wrot Cypress Door Frames size 100 x 50mm with a suitable rebate to receive hinged door panel, including suitable mild steel cramps fixed to back of frame and fixing to door opening size and all necessary woodwork finishes (prepare, knot, prime, stop and apply two undercoats and one finishing coat hard gloss paint to woodwork):-
5.1 | Frame to fit door opening 900mm wide x 2400mm high | Nr | 5
PAGE TOTAL CARRIED TO BILL COLLECTION PAGE
DOORS
Panelled Doors
50mm Thick Prime Grade Cypress Panelled Door With 50 x 100mm Stiles and Top Rails,50 x 150mm Middle and Bottom Rails and Infill Panels in 50 x 100mm T & G battens (See Door Details in Appendix) :-
5.2 | Door size 800 x 2030 mm high with 990 x 140mm Georgian wired clear glass view panel. | Nr | 5
Fanlights
Fanlight Panel in-filled with 5mm thick Frosted Glass with a Clear Pattern and With 12mm Thick Hardwood Lipping All Round:-
5.3 | Fanlight panel size 875mm wide x 275mm high | Nr | 5
Wrot Cypress
5.4 | 20 x 20mm Quadrant | m | 29
5.5 | 50 x 15mm Architrave | m | 51
6 | IRONMONGERY
SUPPLY and afterwards Fix the following Ironmongery with Matching Screws as Described:-
6.1 | Pairs 100 mm Stainless steel butt hinges | Nr | 10.5
6.2 | Briton door closer (240 secs) | Nr | 7
6.3 | Three-lever mortice lock as "Union" Ref: 2279 complete with set of anodized aluminium lever handles as "Union" Ref.681-06-02 | Nr | 3
6.4 | Two-lever mortice lock as "Union" Ref: 2279 complete with set of anodized aluminium lever handles as "Union" Ref.681-06-02 | Nr | 7
6.5 | Stainless steel buffer coat hooks | Nr | 3
6.6 | Pair of Stainless steel lever handles | Nr | 10
6.7 | Stainless steel kicking plate size 800 x 200mm | Nr | 2
6.8 | Rubber door stop fixed to floor or wall with screw | Nr | 10
6.9 | Pairs 75mm. Brass butt hinges | Nr | 16
6.1 | 75mm. Barrel bolt | Nr | 16
6.11 | 100mm D-pull handles | Nr | 16
PAGE TOTAL CARRIED TO BILL COLLECTION PAGE
6.12 | Cupboard door lock | Nr | 8
6.13 | Approved drawer knobs | Nr | 7
Steel Casement Windows
Supply and Fix the following Standard Section Steel Casement Windows, including 4mm Thick Clear Sheet Glass glazed to Steel Casements with putty, complete with opening accessories, including building in lugs to jambs and head and water-proofing and filling around opening with approved compound; and including burglar-proofing fabricated from 12 x 12mm mild steel square bars at 150mm centres vertically and 150mm horizontally and fixed internally to surrounding wall with 12mm mild steel fish-tailed lugs at maximum 600mm centres; all finished with three coats oil paint, :-
6.14 | Window size 1797 x 1197mm high with 1 No. fixed and 2 No. side hung opening bottom sashes and with 2 No. fixed and 1 No. top-hung top ventilators with permanent ventilator hood over (W1) | Nr | 5
6.15 | Window size 1197 x 1397mm high with 1 No. fixed and 1 No. side hung opening bottom sashes and with 1 No. fixed and 1 No. top-hung top ventilators with permanent ventilator hood over (W3) | Nr | 2
6.16 | Window size 597 x 1197mm high with 1 No. fixed bottom sashes and with 1 No. top-hung top ventilators 200mm high with permanent ventilator hood over (W4) | Nr | 3
Pressed Metal Louvre Doors
Supply and Fix the following Pressed Metal Louvre Doors with 100 x 25mm Stiles and Top & Bottom Rails, 150 x 25mm Middle Rail and 50 x 25mm Metal Infill Louvres and 100 x 25mm Pressed Metal Frames, Including Hinges, Pad Bolts and Tower Bolts, All To Manufacturer's Details, with one coat lead oxide primer complete with three lever mortice lock including bedding and pointing around frames in cement mortar:-
6.17 | Single door size 900 x 2400 mm high | Nr | 3
7 | FITTINGS
The following in 1No. Laboratory Fitting 600mm wide x 900mm high and overall 6900 mm girth
7.1 | 75mm Thick reinforced Concrete Class 20/20mm worktop | m2 | 5
7.2 | Mesh Reinforcement Ref. A 142 in concrete top slab. | m2 | 5
7.3 | Sawn formwork as described to horizontal soffites of worktop | m2 | 5
PAGE TOTAL CARRIED TO BILL COLLECTION PAGE
7.4 | Ditto to edges 75-150mm girth | m | 6
7.5 | 20mm Thick cement and sand (1:4) screed to top and sides of worktop | m2 | 5
7.6 | 12.5mm Thick gauged cement plaster to horizontal soffites of worktop | m2 | 4
7.7 | Prepare and apply two coats plastic emulsion paint to plastered horizontal soffites of worktop | m2 | 4
7.8 | Form groove 100mm deep in masonry wall to receive 75mm edge of concrete bench, build in last and make good | m | 7
7.9 | 125mm Concrete (1:3:6) in benching | m2 | 4
7.1 | Formwork to edge of benching 75-150mm. high | m | 6
7.11 | 100mm Thick solid concrete block walling in gauged cement mortar | m2 | 1
7.12 | 100 x 19mm High cement and sand skirting | m | 3
7.13 | 12.5mm Thick gauged cement plaster to walls | m2 | 2
7.14 | Prepare and apply two coats plastic emulsion paint to plastered walls | m2 | 2
7.15 | 50 x 25mm (finished) Wrot prime grade cypress bearer | m | 3
7.16 | 50 x 25mm (finished) Wrot prime grade cypress bearer, plugged | m | 12
7.17 | 75 x 32mm Wrot prime grade cypress door frame, plugged | m | 20
7.18 | 25mm Blockboard shelves | m2 | 3
7.19 | 25mm Blockboard double door overall size 825 x 675mm high in two equal leaves, each leaf hardwood lipped all round | Nr | 3
7.20 | Ditto overall size 950 x 675mm high in two equal leaves, each leaf hardwood lipped all round | Nr | 3
7.21 | Prepare and apply one coat aluminium primer before fixing to wood surfaces 0 - 100mm girth | m | 32
7.22 | Prepare, knot, prime, stop and apply three coats first quality gloss paint to wood surfaces 100 - 200mm girth | m | 20
7.23 | Ditto general surfaces | m2 | 4
7.24 | Drawer size 550mm wide (front) x 500mm long and 150mm deep with 70 x 20mm sides and back, 90 x 20mm front (all finished sizes) and 5mm plywood bottom tongued all round | Nr | 6
PAGE TOTAL CARRIED TO BILL COLLECTION PAGE
7.25 | 12x12mm (finished) Wrot camphor drawer runners | m | 6
7.26 | 25 x 25mm (finished) Wrot camphor lipping tongued in and glued to edge of blockboard | m | 11
7.27 | 12mm Cement and sand screed to benching steel trowelled smooth | m2 | 4
The following in 1No. Tea Room Fitting 600mm wide x 900mm high and overall 2000 mm girth
7.28 | 75mm Thick reinforced Concrete Class 20/20mm worktop | m2 | 1
7.29 | Mesh Reinforcement Ref. A 142 in concrete top slab. | m2 | 1
7.30 | Sawn formwork as described to horizontal soffites of worktop | m2 | 1
7.31 | Ditto to edges 75-150mm girth | m | 2
7.32 | 20mm Thick cement and sand (1:4) screed to top and sides of worktop | m2 | 1
7.33 | 12.5mm Thick gauged cement plaster to horizontal soffites of worktop | m2 | 1
7.34 | Prepare and apply two coats plastic emulsion paint to plastered horizontal soffites of worktop | m2 | 1
7.35 | Form groove 100mm deep in masonry wall to receive 75mm edge of concrete bench, build in last and make good | m | 2
7.36 | 125mm Concrete (1:3:6) in benching | m2 | 1
7.37 | Formwork to edge of benching 75-150mm. high | m | 2
7.38 | 100mm Thick solid concrete block walling in gauged cement mortar | m2 | 1
7.39 | 100 x 19mm High cement and sand skirting | m | 1
7.40 | 12.5mm Thick gauged cement plaster to walls | m2 | 1
7.41 | Prepare and apply two coats plastic emulsion paint to plastered walls | m2 | 1
7.42 | 50 x 25mm (finished) Wrot prime grade cypress bearer | m | 1
7.43 | 50 x 25mm (finished) Wrot prime grade cypress bearer, plugged | m | 3
7.44 | 75 x 32mm Wrot prime grade cypress door frame, plugged | m | 4
7.45 | 25mm Blockboard shelves | m2 | 1
PAGE TOTAL CARRIED TO BILL COLLECTION PAGE
7.46 | 25mm Blockboard double door overall size 875 x 675mm high in two equal leaves, each leaf hardwood lipped all round | Nr | 1
7.47 | Ditto overall size 950 x 675mm high in two equal leaves, each leaf hardwood lipped all round | Nr | 1
7.48 | Prepare and apply one coat aluminium primer before fixing to wood surfaces 0 - 100mm girth | m | 7
7.49 | Prepare, knot, prime, stop and apply three coats first quality gloss paint to wood surfaces 100 - 200mm girth | m | 7
7.50 | Ditto general surfaces | m2 | 1
7.51 | Drawer size 550mm wide (front) x 500mm long and 150mm deep with 70 x 20mm sides and back, 90 x 20mm front (all finished sizes) and 5mm plywood bottom tongued all round | Nr | 1
7.52 | 12x12mm (finished) Wrot camphor drawer runners | m | 1
7.53 | 25 x 25mm (finished) Wrot camphor lipping tongued in and glued to edge of blockboard | m | 3
7.54 | 12mm Cement and sand screed to benching steel trowelled smooth | m2 | 1
8 | EXTERNAL WALL FINISHES
External Rendering in 12mm (minimum) Thick in Two Coats, Undercoat Comprising Cement - Sand (1:5) and Finishing Coat Comprising Cement- Sand (1:5) Finished with a Dry Wood Float:-
8.1 | Rendering to blockwork surfaces | m2 | 5
8.2 | Ditto to concrete surfaces | m2 | 52
9 | INTERNAL WALL FINISHES
Internal Plaster in 12mm (minimum) Thick in Two Coats, Undercoat Comprising Cement- Lime putty- Sand (1:2:9) and Finishing Coat Comprising Cement- Lime putty- Sand (1:1:6) Finished Smooth with a Steel trowel:-
9.1 | Plaster to vertical concrete or blockwork surfaces | m2 | 155
9.2 | Ditto to reveals of openings | m2 | 26
Screeds and Backing
Bonded cement and sand (1:4) screed bed in one coat, well bonded to concrete base as described:-
9.3 | 45mm Thick screed laid to falls to receive coloured floor tiles | m2 | 78
9.4 | Ditto but to receive 100mm high skirting | m | 81
PAGE TOTAL CARRIED TO BILL COLLECTION PAGE
Bonded cement and sand (1:4) Backing 12mm (minimum) Thick in one coat, well bonded to concrete or blockwork with approved plasticiser as described:-
9.5 | Backing laid vertical to receive coloured ceramic wall tiles | m2 | 10
Wall Tiles
Coloured Ceramic Wall Tiles from Saj Co. as supplied by M/s Tile & Carpet Centre, or other equal and approved
9.6 | 200 x 300mm Thick coloured wall tiles laid on backing (measured separately) and joints filled in approved filler to match colour of tiles. | m2 | 10
Sundries
9.7 | PVC tiling edge to external corners of tiles (Provisional) | m | 50
10 | FLOOR FINISHES
Ceramic Floor Tiling
Coloured Ceramic Floor Tiles from Saj Co. as supplied by M/s Tile & Carpet Centre, or other equal and approved
10.1 | 300 x 300mm Tiles laid on screed (measured separately) and joints filled in approved filler to match colour of tiles. | m2 | 78
10.2 | Ditto but laid as skirting 100mm high | m | 81
11 | ROOF FINISHES
Concrete, Double Roll, Single Lap Interlocking Tiles fixed on sloping concrete roof including all necessary securing in position :-
11.1 | Tiles roof covering on and including sawn cypress (Grade 2) battens size 50 x 50mm at 300mm centres and pressure impregnated with approved preservative. | m2 | 135
11.2 | Half round butt jointed ridge tiles bedded, jointed and pointed in cement mortar to match colour of tiles. | m | 21
11.3 | Gauge 28 GCI sheet underlay over the rafters, lapped 300mm vertically and 150mm horizontally laid under battens | m2 | 270
PAGE TOTAL CARRIED TO BILL COLLECTION PAGE
12 | CEILING FINISHES
CHIPBOARD CEILING
12mm thick approved chipboard to BS 2604, Part 2, density 480-640kgs, per square meter in sheets size 2400 x 1200mm fixed to and including 50 x 50mm sawn cypress Grade 2 battens at 600mm centres in both directions complete with gauge jointing material
12.1 | Horizontal ceiling fixed to underside of trusses | m2 | 62
12.2 | 12mm Cornice 50mm high, plugged | m | 95
12.3 | Extra over ceiling lining for forming removable access trap door size 600 x 600mm with 100 x 38 mm sawn treated cypress trimming joists between tie beams,120 x 20mm (finished ) wrot cypress frame all round and 20mm blockboard removable panel set loose on top of framing. | m | 95
Eaves
T & G uPVC Ceiling
12.4 | uPVC T&G ceiling fixed on underside of eaves including all fittings & joinery | m2 | 57
SUNDRIES
12.6 | Prepare, and apply three coats clear wax polish to timber surfaces | m2 | 47
13 | PLUMBING AND DRAINAGE
Builders Work in Connection with Sanitary Fittings
Allow for cutting and leaving all necessary holes, notches, mortices, sinkings and chases both in the structure and its finishes and for all making good in connection with the following (All Provisional): -
13.1 | White vitreous china squatting level washdown W.C. suite complete | Nr | 2
13.2 | White vitreous china washbasin complete | Nr | 2
13.3 | Shower unit complete | Nr | 1
13.4 | Local stainless steel sink with double bowls and double drainer complete | Nr | 1
13.5 | Mirror size 600 x 600mm plugged and screwed to wall | Nr | 2
13.6 | Toilet roll holder | Nr | 2
PAGE TOTAL CARRIED TO BILL COLLECTION PAGE
13.7 | Recessed soap tray | Nr | 1
13.8 | Chrome plated shower rail size 25mm diameter x 900mm long complete with mixers | Nr | 1
Builders Work in Connection with Water and Drainage services
13.9 | Chase wall for small pipe and make good wall and its finishes | m | 28
13.1 | Chase wall for large pipe and make good wall and its finishes | m | 2
13.11 | Hole through 100mm walling for small pipe and make good | Nr | 2
13.12 | Hole through 200mm wall for small pipe ditto | Nr | 3
13.13 | Hole through 150mm reinforced concrete floor slab for large pipe ditto | Nr | 2
Water supply to tank
PN20 PPR pipes and PPR encased brass fittings complying with relevant ISO standards. Pipe & pipe fitting dimensions refer to outside diameter
13.14 | 20mm diameter pipe fixed & jointed in /on wall, ceiling or duct | m | 13
13.15 | 25mm diameter overflow pipe | m | 1
13.16 | 20mm diameter elbow | Nr | 3
13.17 | 20mm diameter bronze gate valves to BS5454 | Nr | 1
Ball valve
13.18 | 32mm diameter medium pressure ball valve as "PORTSMOUTH" type or approved equivalent with brass stem and plastic float, screwed to threaded socket of tank including union | Nr | 1
Water distribution from tank to fittings
PN20 PPR pipes and PPR encased brass fittings complying with relevant ISO standards. Pipe & pipe fitting dimensions refer to outside diameter
13.19 | 20mm diameter pipe fixed & jointed in /on wall, ceiling or duct | m | 14
13.2 | 20mm diameter elbow | Nr | 5
13.21 | 20mm diameter threaded elbow | Nr | 4
13.22 | 20mm diameter equal tee | Nr | 5
13.23 | 20mm diameter plug | Nr | 1
PAGE TOTAL CARRIED TO BILL COLLECTION PAGE
13.24 | 15mm diameter PN20 connector to W.C cistern, Urinal bowl, Wash basins and kitchen sink | Nr | 6
13.25 | 15mm diameter bronze gate valves to BS5454 | Nr | 1
Roof Water storage tanks
13.26 | 1000 Litres capacity plastic water storage tank, dimension 55mm diameter and 90mm height, on roof slab and complete with cover and having screwed connections for inlet (20mm), outlets (20mm), overflow (25mm) and 20mm drain . As "Roto" or approved equivalent. | Nr | 1
Foul/Waste drainage from fittings
uPVC pipe and pipe fittings to BS4460 and BS4551
13.27 | 40mm Waste fittings | Nr | 2
13.28 | 40mm Bottle trap | Nr | 2
13.29 | 40mm Outlet pipe | m | 2
13.3 | 15mm Bip tap | Nr | 1
13.31 | 15mm Bip tap | Nr | 1
13.32 | 32mm Waste fittings | Nr | 2
13.33 | 32mm Bottle trap | Nr | 2
13.34 | 32mm Outlet pipe | m | 2
13.35 | 15mm Bip tap | Nr | 2
13.36 | 100mm diameter long radius bend with duct foot | Nr | 2
13.37 | Vent pipe fabricated from .3.40 m x 100mm diameter fixed and jointed on/in wall or ceiling including 300x300mm GMS paddle flanges | Nr | 1
14 | SANITARY FITTINGS
Supply, deliver and install the following appliances including their support brackets, screws etc and their connection to water supply, waste/soil drainage and electrical supply.
Shower
14.1 | Hygiene hand spray (Arabian shower) complete with 1.5m CP flexible hose | Nr | 1
Mirrors
14.2 | 610 x 457 x 6mm thick bevelled plate glass mirrors with chromium plated domed screws complete with 5mm thick foam back rest. | Nr | 2
PAGE TOTAL CARRIED TO BILL COLLECTION PAGE
Soap Dispenser
14.3 | 130x231x231mm High, sturdy impact resistant ABS plastic lockable case, broad dispensing lever that can also be actuated by elbow, inspection window, screw to wall, 1 Litre Liquid soap dispenser including initial charge. As "Starmix" Model No. SP 1. | Nr | 2
Hand Drier
14.4 | The hand drier shall be operated by infrared sensor which switches on when hands are placed are placed under the hot- air outlet. The machine switches off when the hands are withdrawn or after 40secs. It shall be capable of delivering 36Litres/sec of warm air at 50o C above ambient temperature at an average speed of 17m/s and a relative drying time of 35 seconds with a power supply of 2.2Kw 240V,50Hz. It shall be as "Starmix" Automatic Hand Drier Model No.T50E. | No | 2
14.5 | Allow for electrical connection from DP switch | Item | 1
14.6 | Allow for the testing and commissioning of the sanitary fittings and accessories to the satisfaction of the Engineer | sum | 1
Sanitary appliances
All sanitary appliances shall be supplied as complete units with all fittings, fixtures , waste grids & traps and shall be as specified or approved equal (as per tendered document)
14.7 | Close coupled water closet as "(No Suggestions) Option" with cistern comprising *WC bowl with horizontal outlet with S trap outlet connector ,6 litre cistern with fittings & CP lever , *seat & cover | Nr | 2
14.8 | Wall mounted washbasin as "Twyfords Entice 575" with one tap & 32mm waste grid *basin mixer as "Europath Astra" with aerator & pop -up waste.*32mm CP bottle trap with tail pipe, cap-nut & wall flange as "Cobra" 340 &C-342/1/2/3 | Nr | 2
Stainless steel sink
14.9 | Local stainless steel sink size 1000 x 500mm with single bowl and double drainer complete with 40mm waste, plug, and chain and one "Bricon" chromium plated bib tap type No. 615/041 marked "cold" | Nr | 1
14.1 | Black vulcathene laboratory sink internal size 450 x 300 x 200mm deep as "ALLIED FOUNDERS UK Model 602" complete with waste fitting and butyl rubber sealing gasket including fixing into prepared hole in concrete worktop. | Nr | 1
PAGE TOTAL CARRIED TO BILL COLLECTION PAGE
Builders Work in Connection with Electrical Installations
Allow for cutting and leaving all necessary holes, notches, mortices, sinkings and chases both in the structure and its finishes and for all making good in connection with the following in concealed conduits or cables ( All Provisional) :
14.11 | Lighting points | Nr | 15
14.12 | Switch points | Nr | 15
14.13 | Socket outlet points | Nr | 5
14.14 | Twin socket outlets | Nr | 5
14.15 | Fire alarm points | Nr | 1
14.16 | Data outlet points | Nr | 1
14.17 | Telephone points | Nr | 1
14.18 | Isolator points | Nr | 1
14.19 | Main distribution board | Nr | 1
14.2 | Consumer units and distribution board points | Nr | 1
15 | LIGHTING INSTALLATION
Final sub-circuits from consumer unit in a cable and conduit installation comprising concealed heavy gauge PVC conduit, 1.5 mm2 PVC insulated copper cables, 1.5mm2 copper earthing cable including all accessories and fittings.
15.1 | Lighting point | Nr | 15
15.2 | 6 Amp one gang one way switch as Crabtree | Nr | 15
Light fittings complete with accessories, lamps and tubes, 1.5 mm2 three core heat resisting cables and wiring to an adjacent lighting point and fixing
15.3 | 1x36W single fluorescent batten fitting. As Micromark Standard Batten Range Cat No MM8191 | Nr | 15
16 | GLAZING
6mm Thick Tinted Glass To BS 9512, Free From Flaws, Bubbles, Specks and Other Imperfections, and glazing to aluminium windows or doors in panes:-
16.1 | 1.00 - 1.50 Square metres | m2 | 16
PAGE TOTAL CARRIED TO BILL COLLECTION PAGE
17 | PAINTING AND DECORATING
Prepare, prime and apply three coats eggshell paint :
Externally on:-
17.1 | Metal door (measured flat overall) | m2 | 7
17.2 | Metal window (measured flat overall) | m2 | 16
Internally on:-
17.3 | Metal door (measured flat overall) | m2 | 7
17.4 | Metal window (measured flat overall) | m2 | 16
Prepare and apply one coat aluminium primer before fixing to :-
17.5 | Backs of wood 0 - 100mm girth | m | 80
17.6 | Backs of wood 100 - 200mm girth | m | 40
Prepare, knot, prime, stop and apply two undercoats and one finishing coat hard gloss paint to woodwork:-
Internally on:-
17.7 | General surfaces of doors (measured flat overall) | m2 | 23
17.8 | General surfaces of fascia board | m2 | 54
17.9 | Surfaces 0 - 100mm girth | m | 80
17.1 | Surfaces 100 - 200mm girth | m | 40
17.11 | Surfaces 200 - 300mm girth | m | 6
Prepare and apply three coats of exterior first quality silk vinyl washable paint to :-
17.12 | Rendered blockwork surfaces | m2 | 5
17.13 | Rendered concrete surfaces | m2 | 52
Prepare and apply three coats of interior first quality silk vinyl washable paint to :-
17.14 | Plastered vertical concrete or blockwork surfaces | m2 | 155
17.15 | Plastered reveals of openings | m2 | 26
PAGE TOTAL CARRIED TO BILL COLLECTION PAGE
18 | PROVISIONAL SUMS
18.1 | Allow for the Prime Cost (P.C.) Sum of Shillings Two Hundred Thousand (Kshs. 200,000) for SPECIALISED KITCHEN FITTINGS AND OFFICE FURNITURE INSTALLATIONS to be executed complete by Nominated Sub-Contractor.A29 | Item | P.C
18.2 | Allow for P.C. sum of Kshs. 2,000,000 for equiping the Laboratory with requisite equipment, reagent, apparatus, etc. all as directed by the Engineer. | Item | P.C
18.3 | Allow ….% for profit, administration attendance overheads, etc. for items 18.1 and 18.2 above. | % | 18%
PAGE TOTAL CARRIED TO BILL COLLECTION PAGE

## Collection Sheet 3.12
TETU-AGUTHI WATER SUPPLY PROJECT
BILL No. 3.12
PAGE TOTALS COLLECTION SHEET
Amount
Kshs.
Page Total, Page 1 of 18
Page Total, Page 2 of 18
Page Total, Page 3 of 18
Page Total, Page 4 of 18
Page Total, Page 5 of 18
Page Total, Page 6 of 18
Page Total, Page 7 of 18
Page Total, Page 8 of 18
Page Total, Page 9 of 18
Page Total, Page 10 of 18
Page Total, Page 11 of 18
Page Total, Page 12 of 18
Page Total, Page 13 of 18
Page Total, Page 14 of 18
Page Total, Page 15 of 18
Page Total, Page 16 of 18
Page Total, Page 17 of 18
Page Total, Page 18 of 18
Bill No. 3.10 Total Exclusive of VAT Carried to Section 3 Summary Sheet

## Site and ancilliary
TETU-AGUTHI WATER SUPPLY PROJECT
BILL No. 3.13
TREATMENT WORKS - SITE AND ANCILLARY WORKS
ITEM | DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
No. |  |  |  | Kshs | Kshs. | cts
1 | SITE CLEARANCE AND GENERAL EXCAVATION
Site Clearance of Work Area of Treatment Works Site; Rate to Include for Carting Away and Disposing Cleared Material to tips identified by contractor and approved by the Engineer.
NOTES:
At present, the Treatment Works Site is covered entirely by shrubs.
1.1 | Clear area within the treatment works site of all grass, bushes, shrubs, hedges and grub up roots. | ha | 1.25
1.1 | Demolish and remove all artificial objects which are above the natural ground surface including buildings and any other artificial structure and cart away to spoil or stack on site foe reuse as directed by the engineer. | LS
1.3 | Cut down trees, grub up roots and burn debris. Girth n.e. 1.2m (Provisional) | Nr | 10
Top Soil Stripping
1.4 | Excavate over site for roads, buildings, etc., average 150 mm deep to remove vegetable soil and stack part of material for use as and where directed by the Engineer, cart away surplus to tips. | m2 | 5000
Earthworks and Grading
1.5 | Excavate below stripped surface to formation level of roads and footpaths as indicated on drawngs, including compaction of area, stack approved material for reuse as fill and cart away surplus to tips identified by the Contractor in liaison with the Local Authority, all as directed by the Engineer. | m3 | 500
1.6 | Fill using approved excavated material, compact in 150mm layers as specified under roads and verges | m3 | 200
1.7 | Excavate below stripped level to finished ground level area around Backwash Lagoon and Sludge Drying Beds and other miscellaneous areas, including compaction area,stack approved material for re-use as fill and cart away surplus to tips identified by the Contractor in liaison with the Local Authorities. Depth of excavation n.e. 1.5m | m3 | 120
1.8 | Extra charge over rate shown in items 1.5 and 1.7 for excavation in rock Class 'A' (Provisional) | m3 | 40
1.9 | Extra charge over rate shown in items 1.5 and 1.7 for excavation in rock Class 'B', blasting not allowed (Provisional) | m3 | 60
PAGE TOTAL CARRIED TO SECTION COLLECTION SHEET
1.1 | Extra charge over rate shown in items 1.5 and 1.7 for excavation in rock Class 'C', blasting not allowed (Provisional) | m3 | 30
1.11 | Fill using approved excavated material and compact in 150 mm layers as specified around structures | m3 | 350
1.12 | Spread top soil stacked on site (item 1.4) for reuse. Level and prepare for grassing and landscaping. | m2 | 2500
1.13 | Provide and plant approved grass in areas prepared under the item above and maintain until it takes roots | m2 | 2500
2 | ROADS (INTERNAL ROADS) & FOOTPATHS
Kerbs and Channels
2.1 | Provide, lay and joint 255 mm x 125 mm precast concrete kerbs on and including 250 mm x 100 mm Class 15/20 concrete foundation and haunch 125 mm thick including all excavation, shuttering, jointing and bedding as specified. | m | 90
2.2 | E.O. Item for kerbs laid to radius n.e. 20 m | m | 30
2.3 | Provide, lay and joint 125 mm x 100 mm precast concrete channels on and including 225 mm x 125 mm Class 15/40 concrete bed and haunch 100 mm thick including all excavation, shuttering, jointing and bedding as specified. | m | 75
2.4 | E.O. Item for channels laid to radius n.e. 6.0 m | m | 25
Roads and Foot Paths
Sub-Base and Base Courses: Provide, Lay and Compact:
2.5 | Hand packed hardcore compacted to CBR not less than 30 up to formation level (where road is in fill) | m² | 700
2.6 | Base 200mm thick crusher run or quarry chips (hand packed), including for watering and stone dust blinding as directed. | m2 | 700
2.7 | Provide and apply approved weed killer / herbicide to road surface in accordance with manufacturer's instructions | m2 | 700
Concrete Block Paving (as Manufactured by Cabro Works Ltd or Other Approved Supplier)
2.8 | Normal loading blocks size 210mm x 105mm x 60mm (Minimum strength 45N/m2) laid on and including 50mm screeded sand bed and compacted by surface vibration | m2 | 700
Murram Roads
2.9 | Provide, lay and compact to a minimum of 150mm thickness and CBR not less than 30, approved hardcore fill over Road Formation Surface | m2 | 350
PAGE TOTAL CARRIED TO SECTION COLLECTION SHEET
2.1 | Provide, lay and compact murram wearing course compacted to a minimum of 150mm (consisting of well graded gravel stabilised with 3% cement and compacted using 8-10 tonne roller to the satisfaction of the Engineer including maintenance during construction period | m2 | 350
2.11 | Provide and apply approved weed killer to murram base as specified. | m2 | 350
Road Markings
2.11 | Provide all materials and put road markings on sides, edges of roads and parkings as per Ministry of Public Works Specifications, using approved road marking paint. | m | 150
Footpaths
Provide and lay:
2.12 | 100mm thick murram sub-base for footpaths, well compacted | m2 | 300
2.13 | 50mm thick concrete bed for footpath (Class 15-1:4:8) | m2 | 300
2.14 | Precast concrete paving in 600mm x 600mm x 50mm slabs jointed and grouted up in lime and sand (1:3) | m2 | 300
3 | FENCING AND GATES
3.1 | Excavate for post holes, provide all materials and construct chain link fence on concrete posts at 3 m centres all including straining posts at every 10th post and additional posts at corners. | m | 600
3.2 | Provide all materials and construct metal gate 4.0 m wide with 1Nr 915 mm wide pedestrians gate including 4Nr pillars | Nr | 1
3.3 | -Ditto - but 4.0m wide gate including 2Nr pillars, footing, etc. | Nr | 1
3.4 | -Ditto - but 2.0m wide pedestrian gate including 2Nr pillars, footing, etc. | Nr | 1
4 | SURFACE WATER DRAINAGE
Precast Concrete Drains
4.1 | Excavate trench for precast concrete invert block drain Type 'A' as shown on Drg. NO. M407/SD/21, including trimming of sides and cart excavated matrial to tips. Depth to invert n.e. 1.0m | m | 350
4.2 | -Ditto - but depth to invert n.e 1.5m | m | 20
4.3 | E.O. items 4.1 and 4.2 but with 2 courses (one each side) of precast side slabs | m | 200
PAGE TOTAL CARRIED TO SECTION COLLECTION SHEET
4.4 | -Ditto - but with 4 courses (two each side) of precast concrete side slabs | m | 140
4.5 | -Ditto - but with 6 courses (three each side) of precast concrete side slabs (Provisional) | m | 10
4.6 | Provide, lay and joint precast concrete invert block drain Type 'A' on 100mm murram bed, including 75mm murram filling both sides for height of block. | m | 350
4.7 | E.O. item 4.6 above for provide, lay and joint two courses (one each side) of precast concrete side slabs to Type 'A' drain on 75mm thick compacted murram bed. | m | 200
4.8 | -Ditto - but with 4 courses (two each side) | m | 140
4.9 | -Ditto - but with 6 courses (three each side) (provisional) | m | 10
4.1 | Provide, lay and joint to any radius, precast concrete invert block drain on 100mm murram bed including 75mm murram filling both sides for height of block. Price to include for all cutting, waste, etc. | m | 15
4.11 | E.O. item 4.10 above for provide, lay and joint two courses (one each side) of precast concrete side slabs to invert block drain on 75mm block compacted murram bed. Price to include for all cutting, waste, etc. | m | 10
4.12 | -Ditto - but with 4 courses (two each side) | m | 5
Earth Drains
4.14 | Excavate trapezoidal earth drains type 1 as shown on Drg. No. M407/SD/16 to the lines and levels directed by the Engineer. Allow for trimming of sides to correct slopes and cart excavated material to tips. Depth to invert n.e. 1.0m | m | 300
4.15 | -Ditto- but depth to invert n.e. 1.5m | m | 200
4.16 | Provide and spread 100mm of approved top soil on the base of sides of the earth drain, rake and level to the requried profiles as directed by the Engineer (Provisional) | m2 | 800
4.17 | Supply and plant approved grass on base and sides of the earth drain and maintenance until it takes root to the satisfaction of the Engineer (Provisional) | m2 | 800
Culvert Pipes
4.18 | Excavate trench depth n.e. 2.5 m, supply, lay and joint for 300mm diameter precast concrete ogee pipes including concrete surround, backfill after laying of pipes, compact and cart away surplus material to tips | m | 30
PAGE TOTAL CARRIED TO SECTION COLLECTION SHEET
Headwalls
4.19 | Excavate for, provide all materials and construct 225 mm thick masonry headwalls including concrete Class 15/20 footings, all in accordance with detailed drawings | Nr | 10
5 | CHEMICAL SOAK AWAY PITS
5.1 | Excavate for, provide all materials, construct, test and commission chemical soak away pit including radial arms | Nr | 1
6 | SIGNBOARD
6.1 | Provide all materials and construct signboard . Include for painting, decorating and anchoring of the signboard to the ground using 300mm x 300mm x 600mm deep mass concrete footing, all as detailed | Item | L.S
NOTE: FINAL WORDING ON THE SIGN BOARD TO BE DECIDED IN CONSULTATION WITH THE CLIENT
7 | GUARD HOUSE
7.1 | Provide all materials and construct Guard House Building with electrical distribution, light fittings, etc.,. Include for all finishes, paintings, etc. | Item | L.S
8 | STAFF HOUSES
8.1 | Excavate foundations, supply all materials and construct Staff House (Type B) - 1Nr Unit 76.32 m² 1. Include for building and provision of plumbing works, inspection chambers, sewer pipes, water supply and electrical installation, furniture and other facilities all to the approval of the Engineer. | Item | L.S
8.2 | Excavate foundations, supply all materials and construct Staff Houses (Type C houses) - 2Nr Unit. Each unit 110.205 m² has 2 Nr. Houses. Include for building and provision of plumbing works, inspection chambers, sewer pipes, water supply and electrical installation, furniture and other facilities all to the approval of the Engineer. | Item | L.S
9 | SEPTIC TANKS
9.1 | Supply and install, including excavation, etc, 2 No. Plastic Septic Tank, Each minimum capacity 2.5m3, including Inlet and Outlet Chambers and Pipework, Soak Pit / Radial Arms etc. all as per suppliers instructions ("Septank" from Kentainers Ltd. or approved equivalent) | Item | L.S
PAGE TOTAL CARRIED TO SECTION COLLECTION SHEET
10 | MISCELLANEOUS WORKS
10.1 | Allow a Provisional Sum of Kshs. 1,000,000 to be used as directed by the Engineer for any other works as may be deemed necessary, e.g additional site works to suit ground conditions including reinforced concrete retaining walls, additional surface water drainage, slope stabilization, landscaping works, etc. | Item | P.S
PAGE TOTAL CARRIED TO SECTION COLLECTION SHEET
Note on B108: Mohamed Ibrahim Also provisional
Note on B114: Mohamed Ibrahim: Also Provisional
Note on B164: Mohamed Ibrahim: check on the standard drawing number
Note on B166: Mohamed Ibrahim: insert the correct drawing number

## Collection Sheet 3.13
TETU-AGUTHI WATER SUPPLY PROJECT
BILL No. 3.13
PAGE TOTALS COLLECTION SHEET
Amount
Kshs.
Page Total, Page 1 of 6
Page Total, Page 2 of 6
Page Total, Page 3 of 6
Page Total, Page 4 of 6
Page Total, Page 5 of 6
Page Total, Page 6 of 6
Bill No. 3.12 Total Exclusive of VAT Carried to Section 3 Summary Sheet

## Section 3 Summary Sheet
SECTION 3
TREATMENT WORKS (BILL No. 3.1 - 3.13)
SUMMARY SHEET
Amount
(Kshs.)
Bill No. 3.1 - Stilling Well, Chemical Dosing Channel & Flocculation
| Bill No. 3.2 - Chemical Storage & Mixing Building |  |  | 0
0
| Bill No. 3.3 - Sedimentation Tanks - 4Nr. |  |  | 0
Bill No. 3.4 - Filters, Filter Gallery & Filter Control Room
Bill No. 3.5 - Treated Water Tank
0
Bill No. 3.6 - Chlorine Storage and Mixing Building
Bill No. 3.7 - Back wash Pumps and Pump House
| Bill No. 3.8 - Elevated Backwash Water Tank (150m3) |  |  | 0
Bill No. 3.9 - Backwash Water & Sludge Lagoon and Recirculation Chamber
| Bill No. 3.10 - Sludge Drying Beds |  |  | 0
Bill No. 3.11 - Administration Building
Bill No. 3.12 - Site and Ancillary Works
| Section 3 Total Exclusive of VAT Carried to The Bill of Quantities Grand Summary | 0

## RWM
TETU AGUTHI WATER SUPPLY PROJECT
BILL No. 4.1
RAW WATER GRAVITY MAIN-TETU AGUTHI
ITEM | DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
No. |  |  |  | (Kshs) | (Kshs)
CLASS A: GENERAL ITEM
A26 | Testing of works
A261 | Testing and Commissioning of the Pipeline including provision of all equipment, materials and works necessary for testing such as but not limited to Thrust Blocks, Anchor Blocks,Provision, Transportation and use and disposal of Water, Pipe Fittings,etc. Nominal bore 400mm | m | 16400
A262 | Disinfection of Pipeline ; Flushing with clear water, filling with water containing 0.05g/l Calcium Hypochlorite, left for 24 hours. This includes supply of necessary Equipment, Materials, Chemicals and Water, Measurement of Residual Chlorine, all as specified and safe disposal of disinfecting water to Engineer's approval. | m | 16400
A3 | Method Related Charges
Sections of the Pipeline from the Intake to the t. works is to be laid along the river and is rocky in some sections.
Specific conditions in execution of these Works are deemed to be included in the Contractor's rates. The Contractor will be required to submit Method Statement for execution of works under these specific conditions for approval prior to execution of the works. These include but are not limited to the following: i. No blasting will be permitted in these areas ii. The Contactor to maintain uninterrupted continuity of water supply in existing pipelines iii. Allow for method related costs for dewatering of trenches.
A35 | Cost relating to the above mentioned specific conditions | Item | LS
Allow for method related charges the tenderer feels may be required. These should be idicated below with pricing for each item
A351 | i) | Item | LS
A352 | ii) | Item | LS
CLASS D: DEMOLITION AND SITE CLEARANCE
D1 | General site clearance along the pipeline allignment. | ha | 7
D2 | Tree Cutting (Provisional)
Cut down trees, grub up roots and cart away to tips
D21 | Girth: 0.5 m - 1.0 m | Nr | 250
PAGE TOTAL CARRIED TO BILL COLLECTION PAGE
D22 | Girth: 1.0 m - 2 m | Nr | 200
D23 | Girth 2.0 m - 3 m | Nr | 100
D24 | Girth 3.0 m - 5 m | Nr | 50
Note:- Girth shall be measured 1.0m above ground level
PIPES, FITTINGS AND VALVES
Supply, Transport to site and store in secure place. Include supply of jointing materials, bolts, nuts, gaskets etc as applicable
Transport from Site Store, Lay and Joint Pipes in Trench, include for Excavation, Preparation of Surfaces, Disposal of Excavated Material, Shoring Sides of Excavation Trenches, Backfilling and Final Reinstatement
CLASS I: PIPE WORK - PIPES
I4 | Ferrous Epoxy coated externally or Approved equivalent and cement mortar lined internally socket and spigot pipes - PN 16
Nominal Bore 355 mm in Trenches
I432.3 | Depth not exceeding 1.5m | m | 600
I433.3 | Depth 1.5m - 2.0m | m | 400
I434.3 | Depth 2.0m - 2.5m | m | 120
I435.3 | Depth 2.5m - 3.0m | m | 200
I436.3 | Depth 3.0m - 3.5m | m | 80
The rate quoted Is for supply, transport to site,pressure testing, cleansing and sterilisation of pipes in accordance to specifications, setting out and pegging, laying and jointing of high density polyethylene (HDPE) pipes including excavation and backfilling of trenches, depth not exceeding 2 m. Include for preparation of trench surfaces; upholding sides of the excavation, disposal of excess excavated material, removal of dead services except to the extent that such work is included in classes J, K and L.
HDPE Pipeline
1712.1 | OD 355 mm HDPE PN 10 | m | 4638
1712.2 | OD 355 mm HDPE PN 12.5 | m | 4714
1712.3 | OD 355 mm HDPE PN 16 | m | 2960
1712.4 | OD 355 mm HDPE PN 20 | m | 3852
I5 | uPVC Class "B" Socket and Spigot pipes for Draining of Washouts (Provisional)
Nominal Bore 200mm in Trenches
I512 | Depth not exceeding 1.5m | m | 60
I513 | Depth 1.5m - 2.0m | m | 60
CLASS J: PIPEWORK - FITTINGS AND VALVES - PN20
A-J3 | Ferrous pipe Fittings - Epoxy coated externally or Approved equivalent and cement mortar lined internally socket and spigot pipes
A-J31 | Plain Ended Bends
A-J313 | Nominal bore 355mm
A-J313.3 | ND 355mm
A-J313.3.1 | 11.25° | Nr | 30
A-J313.3.2 | 22.5° | Nr | 20
A-J313.3.3 | 30° | Nr | 10
A-J313.3.4 | 45° | Nr | 5
A-J313.3.4 | 90° | Nr | 2
PAGE TOTAL CARRIED TO BILL COLLECTION PAGE
A-J32 | Junction and Branches
All Flanged Tee
A-J323.3 | ND 355 x ND 200 | Nr | 25
A-J33 | Tapers
All Flanged Concentric Taper
A-J331.1 | ND 200 x ND 80 | Nr | 25
A-J35 | Ferrous Flanged Adaptor
A-J351.1 | ND 350 | Nr | 100
A-J351.2 | ND 200 | Nr | 12
A-J38 | Straight Specials
Flanged Spigot Pipes
A-J383.1 | ND 355 mm, 1.2m long | Nr | 90
A-J383.1 | ND 200mm, 1.2m long | Nr | 20
A-J8 | Valves and Penstocks
A-J81 | All Flanged Gate Valves
Gate Valves for Washouts and line valves to be supplied complete with extension Spindle n.e. 2.0m and Tee- key. Air valve isolating valves to be supplied with wheel only. Contractor's rates to include for this
A-J811.2 | DN 80 | Nr | 25
A-J811.3 | DN 200 | Nr | 20
A-J813.3 | DN 355 | Nr | 8
A-J86 | Air Valves
A-J861.1 | Double Orifice Air Valve
A-J861.2.2 | DN 80 | Nr | 25
PAGE TOTAL CARRIED TO BILL COLLECTION PAGE
CLASS K: PIPE WORK - CHAMBERS AND PIPE WORK ANCILLARIES
Chambers, ducts, culverts, crossings, thrust, anchor blocks, reinstatement and others pipework ancillaries.
Note:- Items for Work in this class shall include:- - Excavation, preparation of surfaces, disposal of surplus excavated material, shoring sides of excavation, backfilling and removal of redundant services. - Concrete, Reinforcement, Formwork, Joints and Finishes. - Tips for disposal of excavated material or debris to be identified by the Contractor in liaison with the Local Authorities.
K21 | IN SITU MASONRY CHAMBERS
Provide all materials and construct Masonry walling Chambers, internal dimensions 1800mm x 1400mm. Include for supply and fixing of removable precast concrete covers, step irons, compacted granular fill, rendering of exposed blockwork etc .
K211 | Depth not exceeding 1.5 m | Nr | 20
K212 | Depth 1.5 - 2.0m | Nr | 25
K6 | Crossings
PAGE TOTAL CARRIED TO BILL COLLECTION PAGE
K682.2 | Allow for crossing existing underground services (specifically community raw water lines, including reistatement to the original status and liason with the relevant body for inspection/approval during execution of the works. Pilot excavation shall be done to establish exact location of any buried services prior to actual excavation. The rate shall be demeed to include for pilot excavations, repairs and reistatement of any damages to the existing buried services as a result of execution of the works. | Item | LS
K8 | Other Pipework Ancillaries
K82 | Supply and fix marker posts along water Main Route, Road Crossings, change of direction, Air valves, Washouts, and valve chambers. | Nr | 50
K87 | Provide all materials and construct Masonry outfall structures on mass concrete plinths at washout drain pipe outlets. | Nr | 20
CLASS L:- PIPEWORK - SUPPORTS AND PROTECTION, ANCILLARIES TO LAYING AND EXCAVATION
L1 | Extras over excavation and backfilling for excavation in Rock. Rate to include carting away and disposal. (Provisional)
L11 | In pipe trench and chambers
L111.1 | Excavation in trench for rock class "A" | m³ | 250
L111.2 | Excavation in trench for rock class "B" | m³ | 480
L111.3 | Excavation in trench for rock class "C" | m³ | 200
Note:- Blasting is NOT permitted for Item L11
L5 | Surrounds
L53 | Imported Selected Fill (Provisional)
Provide, transport to site and place imported selected fill and compact in bed and surround to pipes as specified and where directed by the Engineer.
L533 | To pipes nominal bore: 300 - 600 mm | m³ | 700
PAGE TOTAL CARRIED TO BILL COLLECTION PAGE
L7 | Concrete Support, Thrust Blocks, Stools and Anchor Blocks
Rates to include for excavation, formwork, provision and placing of concrete, backfilling etc
Class 20/20 Mass Concrete
NOTE:- The work includes pipe and fitting fixing
L72 | Volume:- 0.1 - 0.2 m³
L723 | To pipes nominal bore 300 - 600mm | Nr | 2
L73 | Volume:- 0.2 - 0.5 m³
L733 | To pipes nominal bore 300 - 600mm | Nr | 5
L74 | Volume:- 0.5 - 1.0m³
L743 | To pipes nominal bore 300 - 600mm | Nr | 25
L75 | Volume:- 1.0 - 2.0m³
L753 | To pipes nominal bore 300 - 600mm | Nr | 5
PAGE TOTAL CARRIED TO BILL COLLECTION PAGE

## Collection Sheet 4.1
TETU AGUTHI WATER PROJECT
BILL NO. 4.1
PAGE TOTALS COLLECTION SHEET
Amount
Kshs.
Page Total, Page 1 of 6
Page Total, Page 2 of 6
Page Total, Page 3 of 6
Page Total, Page 4 of 6
Page Total, Page 5 of 6
Page Total, Page 6 of 6
Bill No. 2.3 Total Exclusive of VAT Carried to Section 2 Summary Sheet

## INTAKE
TETU- AGUTHI WATER SUPPLY PROJECT
BILL No. 4.2
INTAKE WORKS - INTAKE WEIR, INTAKE CHAMBER AND RIVER BED/BANK PROTECTION WORKS
ITEM | DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
No. |  |  |  | (Kshs) | (Kshs)
A | GENERAL ITEMS
Temporary Works
2.1A275 | River diversion works at intake including construction of cofferdams, etc. Note: Bidder must submit proposed Method Statement for execution of these Works with the Bid. | Item | L.S
Method Related Charges
Method Related Charges for diversion of river and working in water logged area:
2.1A355 | Dewatering | Item | L.S
2.1A357 | Cofferdams | Item | L.S
2.1A380 | Any other method related charges the Bidder feels may be required. These should be indicated below in pricing of each item
Establishment of River Gauging Station
2.1A420 | Provisional Sum for establishment of a River Gauging Station on at the Intake Site as directed by the Engineer. River Gauging Station to be installed within the first 4 Weeks after Mobilization. River Gauging Station to be installed in liaison with the Water Resources Management Authority and in accordance with their Specifications. | Item | P.S
B | GROUND INVESTIGATIONS
Digging and Logging out of Trial Pit (1.0m x 1.0m) Along the Centerline of Intake Weir
2.1B111 | Depth n.e 1.0m | Nr | 1
2.1B112 | Depth 1 - 2m | Nr | 1
2.1B113 | Depth 2 - 3m | Nr | 1
D | DEMOLITION AND SITE CLEARANCE
Site Clearance of Entire Area of the Intake Works Site that will be Fenced; Trees to be Cleared to be Identified by the Engineer: Rate to include for Carting Away and Disposing Cleared Material. Tips to be identified by the Contractor in liaison with Local Authority
2.1D100 | General clearance | ha | 0.2
2.1D210 | Trees of girth 500mm to 1m | Nr | 20
PAGE TOTAL CARRIED FORWARD TO COLLECTION PAGE
2.1D220 | Trees of girth 1m to 2m | Nr | 30
2.1D310 | Stumps of diameter 150mm to 500mm | Nr | 10
2.1D320 | Stumps of diameter 500mm to 1m | Nr | 15
E | EARTHWORKS
Excavations Shall Include for Strutting, Shuttering, Stabilizing Excavated Surfaces and Keeping Excavations Free of Water by Bailing Out, Pumping or Other Means
Excavation for Foundations
Intake Weir and Intake Chamber
2.1E311 | Topsoil depth n.e 0.25m | m3 | 60
2.1E321 | Material other than topsoil or rock depth 0.25 - 1.0m | m3 | 170
2.1E324 | Ditto but depth 1 - 2m | m3 | 221
2.1E325 | Ditto but depth 2 - 5m | m3 | 20
2.1E334 | Rock, depth 0.25 - 2m | m3 | 120
2.1E335 | Ditto but depth 2 - 5m | m3 | 10
General Excavation
Improvement of Riverbed/Bank;
2.1E421 | Topsoil depth n.e 0.25m | m3 | 80
2.1E422 | Material other than topsoil or rock depth 0.25 - 1.0m | m3 | 340
2.1E423 | Ditto but depth 1 - 2m | m3 | 320
2.1E431 | Ditto but depth 2 - 5m | m3 | 640
2.1E432 | Rock, depth n.e 0.25 -2m | m3 | 165
2.1E433 | Ditto but depth 2 - 5m | m3 | 160
Excavation Ancillaries
Trimming of Excavated Surfaces
2.1E512 | Material other than topsoil or rock | m2 | 320
2.1E513 | Trimming rock surfaces | m2 | 80
Disposal of Excavated Material
2.1E532 | Material other than top soil or rock | m3 | 600
2.1E533 | Rock | m3 | 100
PAGE TOTAL CARRIED FORWARD TO COLLECTION PAGE
Filling
Rates to include for compaction in 150mm layers as specified
2.1E614 | Selected Excavated material to intake chamber | m3 | 10
2.1E634 | General Filling on site using selected excavated material | m3 | 500
2.1E635 | General Filling on site using imported natural material other than top soil or rock | m3 | 200
F | IN SITU CONCRETE
Provision of Concrete
Design Mix
2.1F233 | Grade: C15/20 | m3 | 112
2.1F263 | Grade C25/20 | m3 | 165
Placing of Concrete
Mass Concrete
Bases
2.1F511 | C15 Blinding, 75mm thick | m2 | 12
Mass Concrete Lining to Gabions
2.1F581.1 | C15 Concrete, 75mm thick, to vertical faces of rock filled gabions | m2 | 50
2.1F581.2 | C15 Concrete, 75mm thick, to horizontal faces of rock filled gabions | m2 | 50
Reinforced Concrete
Base Slabs
2.1F622 | C25 to Apron, Intake Chamber Base Slab and bases of Retaining Walls | m2 | 89
Suspended Slabs
2.1F632 | C25 to Roof Slab of Intake Chamber | m2 | 3
Walls
2.1F643 | C25 to Intake Chamber Walls and Retaining Walls | m2 | 40
Weir
2.1F680 | C25 to Weir Structure | m2 | 33
PAGE TOTAL CARRIED FORWARD TO COLLECTION PAGE
G | CONCRETE ANCILLARIES
Formwork - Rough finish
Plane Vertical to:-
2.1G144 | Foundation Keys | m2 | 52
2.1G145 | Buried faces of Retaining Walls and Intake Chamber Walls | m2 | 125
Formwork - Fair finish
Plane horizontal to:-
2.1G215 | Soffit of Intake Chamber Roof Slab | m2 | 20
Plane sloping to:-
2.1G225 | Weir - downstream face | m2 | 30
Plane Vertical to:-
2.1G245.1 | Weir - upstream face | m2 | 20
2.1G245.2 | Exposed faces of Retaining Walls and Intake Chamber Walls | m2 | 250
Curved to:-
2.1G254 | Weir Crest | m2 | 10
Rebates:-
2.1G286 | 50 x 50mm Rebates in Roof Slab of Intake Chamber for covers over openings | m | 15
Voids:-
2.1G271 | Small Voids in Intake Chamber Walls for Raw Water Pipe and Scour Pipe, depth n.e. 0.5m | Nr | 2
Reinforcement
Deformed High Yield steel bars to BS 4449
2.1G529 | High Yield Steel Bars, All sizes | t | 15
Concrete Accessories
Finishing of Top Surfaces
2.1G812 | Steel Trowel finish to top surface of Apron and base of Intake Chamber | m2 | 100
Inserts - Rate to Include for Supply and Fixing in Concrete
2.1G831.1 | DN 355 steel plain ended pipe piece for Raw Water Outlet, length n.e 30m, projecting from one surface of Intake Chamber Wall, and with puddle flange at 225mm from one end | Nr | 1
2.1G831.2 | DN 560 steel plain ended pipe piece for Raw Water Outlet, length n.e 30m, projecting from one surface of Intake Chamber Wall, and with blank flange at one end (For future use) | Nr | 1
PAGE TOTAL CARRIED FORWARD TO COLLECTION PAGE
2.1G831.3 | DN 150 steel plain ended pipe piece for Scour, length n.e 8.0m, projecting from one surface of Intake Chamber Wall, and with puddle flange at 225mm from one end. | Nr | 1
2.1G831.4 | DN 200 steel plain ended pipe piece for Scour, length n.e 3.0m, projecting from one surface of Intake Weir. | Nr | 2
I | PIPEWORK - PIPES
Provide and lay pipes in trenches
Raw Water Gravity Main and Scour Pipeline Within Intake Works Site - Approved Lines Ferrous Pipes
2.1I415 | DN 150 in trenches depth n.e 3.0m. | m | 30
2.1I435 | DN 355 in trenches depth n.e 3.0m. | m | 30
J | PIPEWORK - FITTINGS AND VALVES
Rates to include for provision and fixing.
Flexible Coupling
2.1J341 | DN 150 | Nr | 1
2.1J343 | DN 355 | Nr | 2
Penstocks - Hand Operated
2.1J881 | DN 150 with extension spindle, guide brackets, headstock and hand wheel | Nr | 1
2.1J882 | DN 200 with extension spindle, guide brackets, headstock and hand wheel | Nr | 2
2.1J883 | DN 355 with extension spindle, guide brackets, headstock and hand wheel | Nr | 1
2.1J884 | DN 560 with extension spindle, guide brackets, headstock and hand wheel | Nr | 1
N | MISCELLANEOUS METALWORK
2.1N140 | GMS Guardrails, 0.9m high | m | 30
2.1N162 | GMS Fine Screen Guides, made of 60x50x5mm Channel Sections | m | 30
2.1N180 | GMS Open Grating Flooring over access opening for Fine Screens, made of 20mm dia bars welded to 45x45x4mm GMS Angle Frame, size 900mm x 690mm | Nr | 3
2.1N230 | GMS Lockable Covers size 670mm x 670mm for 600mm x 600mm clear manhole openings in roof of Intake Chamber | Nr | 2
PAGE TOTAL CARRIED FORWARD TO COLLECTION PAGE
2.1N299.1 | GMS Plate, size 125x100x5mm thick, welded to Fine Screen Guide Channels and fixed to concrete walls with 1 Nr 12mm dia Rawl Bolt, 100mm long, (rate to include for the bolts, welding to fine screen guide and fixing to concrete wall). | Nr | 84
2.1N299.2 | GMS Locking Bars for Manhole Covers, size 850x50x6mm thick. | Nr | 5
2.1N299.3 | Cast Iron Step Irons fixed to wall of Intake Chamber | Nr | 10
2.1N299.4 | GMS Coarse Screen, size 1600x1300mm, fabricated using GMS bars, dia 20 mm at spacing 40 mm welded to frame fixed with fish tailed lugs into concrete walls. | Nr | 1
2.1N299.5 | GMS Fine Screens, size 2475mm x 560mm, fabricated using 10mm dia M.S. bars at 10mm spacing and 3mm thick plate with 4mm dia. holes, with GMS frame and lifting handles. (Note: 3 Nr fine screens to be installed in the Intake Chamber. 1 Nr fine screen to be supplied and handed over to Employer's Store to be used as standby screen during cleaning / maintenance of the duty screens). | Nr | 4
2.1N299.6 | Provisional Sum for design, fabrication, transport to site and installation of a Metal Girder Bridge across the intake Note: Contractor to obtain Quotations and submit to the Engineer, Design Calculations and Workshop Drawings of Bridge from a reputable Steel Fabricator for approval before fabrication and delivery. | Item | P.S
X | RIVER BED AND BANK PROTECTION WORKS
Rock Filled Gabions
2.1X410 | Box Gabions, size 2m x 1m x 1m, mesh wire 2.0mm diameter, laid in stretches with 0.5m overlap, filled with approved hardcore. | Nr | 250
2.1X420 | Gabion Matresses, thickness 500mm, mesh wire 2.0mm diameter, filled with approved hardcore. | m2 | 150
PAGE TOTAL CARRIED FORWARD TO COLLECTION PAGE

## Collection sheet 4.2
TETU- AGUTHI WATER SUPPLY PROJECT
Tetu- Aguthi Water Supply Project
TOTALS COLLECTION PAGE
Amount
Kshs.
Page Total, Page 1 of 6
Page Total, Page 2 of 6
Page Total, Page 3 of 6
Page Total, Page 4 of 6
Page Total, Page 5 of 6
Page Total, Page 6 of 6
Bill No. 2.1 Total Exclusive of VAT Carried to Section 2 Summary Sheet

## BPT
TETU AGUTHI WATER SUPPLY PROJECT
BILL No. 5.1
BREAK PRESSURE TANKS 3NR (5m3)
ITEM | DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
No. |  |  |  | Kshs | Kshs
1 | BREAK PRESSURE TANK CONSTRUCTION
1.1 | Excavate for, provide all materials and construct masonry Break Pressure Tank, capacity of each 5m3 with covers, all in accordance with approved specifications on and including provision of connections, vent pipes. Allow for testing, finishing and sterilizing of the Tanks and Pipeworks as specified. | Item | L.S
2 | SITE CLEARANCE AND GENERAL EXCAVATION
2.1 | Clear area within the Break Pressure Tank site of all grass, bushes, shrubs, hedges, grub up roots and cart away to tips as directed by the Engineer. | m2 | 144
Top Soil Stripping
1.2 | Excavate over site for buildings, roads, etc.average 150mm deep to remove vegetable soil and stack part of material for use as and where directed by the Engineer, cart away surplus to tips | m2 | 1800
2.2 | Excavate over site for BPT, roads, etc.average 150mm deep to remove vegetable soil and stack part of material for use as and where directed by the Engineer, cart away surplus to tips. | m2 | 50
Earthworks and Grading
2.3 | Excavate approximately 300mm below stripped surface to formation level of roads, footpaths and verges including compaction of areas, stack approved material for reuse as fill and cart away surplus to approved tips identified by he Contractor in liaison with the Local Authorities, as directed by the Engineer. | m3 | 20
2.4 | Fill using approved excavated material, compact in 150mm layers as specified under roads and verges. | m3 | 10
2.5 | -Ditto- around tanks, including cutting and trimming of slopes. | m3 | 5
2.6 | Fill using approved hardcore material and compact in 150mm layers as specified. | m3 | 4
2.7 | Extra charge over rate shown in item 1.3 for excavation in rock Class 'A'. | m3 | 1
2.8 | Extra charge over rate shown in item 1.3 for excavation in rock Class 'B'. | m3 | 1
2.9 | Extra charge over rate shown in item 1.3 for excavation in rock Class 'C'. | m3 | 1
2.10 | Spread top soil stacked on site for reuse (Item 1.2) level and prepare for grassing and landscaping. Plant approved grass and maintain until it takes roots. | m2 | 20
PAGE TOTAL CARRIED TO BILL COLLECTION SHEET
3 | ROADS AND FOOTPATHS
Murram Roads
3.1 | Provide, lay and compact to a minimum of 150mm thickness and CBR not less than 30, approved hardcore fill over Road Formation Surface. | m2 | 35
3.2 | Provide, lay and compact murram wearing course to a minimum of 150mm thickness consisting of well graded gravel stabilised with 3% cement and compacted using 8-10 tonee roller to the satisfaction of the Engineer, including maintenance during construction period. | m2 | 35
2.3 | Provide, lay and compact murram wearing course to a minimum of 150mm thickness consisting of well graded gravel stabilised with 3% cement and compacted using 8-10 tonee roller to the satisfaction of the Engineer, including maintenance during construction period. | m2 | 172
3.3 | Provide and apply approved herbicide / weed killer to murram base as specified. | m2 | 35
Footpaths
Provide and lay:
3.4 | 100mm murram sub-base, well compacted. | m2 | 15
3.5 | 50mm thick concrete bed for footpath (Class 15) | m2 | 15
2.7 | Precast concrete paving in 600mm x 600mm x 50mm slabs jointed and grouted up in lime and sand (1:3) | m2 | 80
3.6 | Precast concrete paving in 600mm x 600mm x 50mm slabs jointed and grouted up in lime and sand (1:3). | m2 | 15
4 | FENCING AND GATES
4.1 | Excavate for post holes, provide all materials and construct chain link fence on concrete posts at 3m centre to centre including straining posts at every 10th post and additional posts at corners. | m | 48
4.2 | Provide all materials and construct metal gate 1.0m wide including pillars, footings, etc. | Nr | 1
5 | SURFACE WATER DRAINAGE
Earth Drains
5.1 | Excavate for earth drains Type '1' to the alignment and levels as shown on drawings and as directed by the Engineer. Allow for trimming of side to correct slopes and cart away excavated material to tips. Depth n.e. 1.5m. . | m | 50
4.2 | Provide and spread 100mm of approved top soil on the base and sides of the earth drain, rake and level to the required profiles as directed by the Engineer (Provisional) | m2 | 300
4.3 | Supply and plant approved grass on base and sides of the earth drain and maintenance until it takes root to the satisfaction of the Engineer (Provisional) | m2 | 300
5.2 | Provide and spread 100mm of approved top soil on the base and sides of the earth drain, rake and level to the required profiles as directed by the Engineer (Provisional). | m2 | 80
PAGE TOTAL CARRIED TO BILL COLLECTION SHEET
5.3 | Supply and plant approved grass on base and sides of the earth drain and maintenance until it takes root to the satisfaction of the Engineer (Provisional) | m2 | 80
Culvert Pipes
5.4 | Excavate trench depth n.e. 2.0m, supply, lay and joint for 300mm diameter precast concrete ogee pipes including concrete surround, backfill after laying of pipes, compact and cart away surplus material to tips. | m | 6
Headwalls
5.5 | Excavate for, provide all materials and construct 225mm thick masonry headwalls including concrete Class 15/20 footings, all in accordance with detailed drawings. | Nr | 2
6 | SCOUR / OVERFLOW DRAINAGE PIPELINE
6.1 | Excavate trench for 200mm dia. uPVC Class 'B' pipe for Scour/ Overflow drainage, backfill after laying of pipes and cart away surplus to tips as directed. Average depth n.e. 2.0m | m | 10
6.2 | Supply, lay, joint and test 200mm dia. uPVC Class 'B' pipes including Type 'BO' bed and surround (mark k). | m | 10
7 | 150mm DIA. PIPEWORK WITHIN BREAK PRESSURE TANK COMPOUND - APPROVED LINED FERROUS PIPES AND FITTINGS
7.1 | Excavate trench for 150mm dia. Pipework within Break Pressure Tank Compount - backfill after laying of pipes and cart away surplus to tips as directed. Average depth n.e. 1.5m. | m | 30
Pipework, Fittings and Valves
Supply, Transport to Site and Store in Secure Place Including Jointing Material, Bolts Gaskets, Packing, Jointing Glues, etc. as Applicable
Inlet Ferrous Pipe Fittings to NP16 Details
7.2 | 355mm dia. Coupling (mark 1) | Nr | 1
7.3 | 355mm dia. Flanged Spigot Pipe 1200mm long (mark 2) | Nr | 1
7.4 | 355 x 355mm dia. all Flanged Radial Tee (mark 3) | Nr | 1
7.5 | 355mm dia. Blank Flange (mark 4) | Nr | 1
7.6 | 355 mm dia Flange Adaptor | Nr | 1
7.7 | 355 mm dia. Flanged Spigot Pipe 1200mm long (mark 6) | Nr | 4
PAGE TOTAL CARRIED TO BILL COLLECTION SHEET
7.8 | 355 mm dia. Coupling (mark 7) | Nr | 2
7.9 | 355mm dia. Plain Ended Pipe 8m long (cut to suit on site) (mark 8) | Nr | 1
7.1 | 355 mm dia. all Fanged 900 Bend (mark 9) | Nr | 3
7.11 | 355 mm dia. Flange Adaptor (mark 10) | Nr | 3
7.12 | 355 mm dia. all Flanged Gate Valve (mark 11) | Nr | 1
7.13 | 355mm dia. Flanged Spigot Pipe 814mm long (cut to suit on site) (mark 12) | Nr | 1
7.14 | 355mm dia. Double Flanged Pipe 575mm long with a Puddle Flange at 262mm from one end (mark 13) | Nr | 1
7.15 | 355mm dia. all Flanged Float Valve (mark 14) | Nr | 1
7.16 | 355mm dia. Flanged Spigot Pipe 739mm long (mark 15) | Nr | 1
Outlet Ferrous Pipe Fittings to NP16
7.17 | 355mm dia. Flanged Bellmouth (mark A) | Nr | 1
7.18 | 355 mm dia. all Flanged 900 Bend (mark B) | Nr | 2
7.19 | 355 mm dia. Flanged Spigot Pipe 1950mm long (cut to suit on site) (mark C) | Nr | 1
7.2 | 355 mm dia. Flange Adaptor (mark D) | Nr | 2
7.21 | 355 mm dia. all Flanged Gate Valve (mark E) | Nr | 1
7.22 | 355 mm dia. Flanged Spigot Pipe 1200mm long (mark F) | Nr | 3
7.23 | 355 mm dia. Coupling (mark G) | Nr | 2
7.24 | 355mm dia. Plain Ended Pipe 8m long (cut to suit on site) (mark H) | Nr | 1
7.25 | 335mm dia. Flange Adaptor | Nr | 1
7.26 | 355 mm dia. Blank Flange (mark J) | Nr | 1
7.27 | 355 x 355 mm dia. all Flanged Radial Tee (mark K) | Nr | 1
7.28 | 355 mm dia. Flanged Spigot Pipe 1200mm long (mark L) | Nr | 1
7.29 | 355 mm dia. Coupling (mark M) | Nr | 1
PAGE TOTAL CARRIED TO BILL COLLECTION SHEET
Overflow Ferrous Pipe Fittings to NP16 Details
7.3 | 150mm dia. Flanged Spigot Pipe 425mm long with a Puddle Flange at 162.5mm from the Spigot End (mark a) | Nr | 1
7.31 | 150mm dia. all Flanged 900 Bend (mark b) | Nr | 1
7.32 | 150mm dia. Flanged Spigot Pipe 439mm long (cut to suit on site) (mark c) | Nr | 1
7.33 | 150mm dia. Flange Adaptor (mark d) | Nr | 1
7.34 | 150mm dia. all Flanged 450 Bend (mark e) | Nr | 1
7.35 | 150mm dia. Flanged Spigot Pipe 502mm long with a Spigot End Bevelled (cut to suit on site) (mark f) | Nr | 1
Washout / Scour Ferrous Pipe Fittings to NP16 Details
7.36 | 150mm dia. Flanged Bellmouth (mark g) | Nr | 1
7.37 | 150mm dia. all Flanged 900 Bend (mark h) | Nr | 1
7.38 | 150mm dia. Double Flanged Pipe 2350mm long (mark i) | Nr | 1
7.39 | 150mm dia. all Flanged Gate Valve to BS 5163 (mark j) | Nr | 1
Transport From Site Store, Install, Test and Commission
Inlet Ferrous Pipe Fittings to NP16 Details
7.4 | 355mm dia. Coupling (mark 1) | Nr | 1
7.41 | 355mm dia. Flanged Spigot Pipe 1200mm long (mark 2) | Nr | 1
7.42 | 355 x355mm dia. all Flanged Radial Tee (mark 3) | Nr | 1
7.43 | 355mm dia. Blank Flange (mark 4) | Nr | 1
7.44 | 355 mm dia Flange Adaptor | Nr | 1
7.45 | 355mm dia. Flanged Spigot Pipe 1200mm long (mark 6) | Nr | 4
7.46 | 355mm dia. Coupling (mark 7) | Nr | 2
7.47 | 355mm dia. Plain Ended Pipe 8m long (cut to suit on site) (mark 8) | Nr | 1
7.48 | 355mm dia. all Fanged 900 Bend (mark 9) | Nr | 3
7.49 | 355mm dia. Flange Adaptor (mark 10) | Nr | 3
PAGE TOTAL CARRIED TO BILL COLLECTION SHEET
7.5 | 355mm dia. all Flanged Gate Valve (mark 11) | Nr | 1
7.51 | 355mm dia. Flanged Spigot Pipe 814mm long (cut to suit on site) (mark 12) | Nr | 1
7.52 | 355mm dia. Double Flanged Pipe 575mm long with a Puddle Flange at at 262mm from one end (mark 13) | Nr | 1
7.53 | 355mm dia. all Flanged Float Valve (mark 14) | Nr | 1
7.54 | 355mm dia. Flanged Spigot Pipe 739mm long (mark 15) | Nr | 1
Outlet Ferrous Pipe Fittings to NP16
7.55 | 355mm dia. Flanged Bellmouth (mark A) | Nr | 1
7.56 | 355mm dia. all Flanged 900 Bend (mark B) | Nr | 2
7.57 | 355mm dia. Flanged Spigot Pipe 1950mm long (cut to suit on site) (mark C) | Nr | 1
7.58 | 355mm dia. Flange Adaptor (mark D) | Nr | 2
7.59 | 355mm dia. all Flanged Gate Valve (mark E) | Nr | 1
7.6 | 355mm dia. Flanged Spigot Pipe 1200mm long (mark F) | Nr | 3
7.61 | 355mm dia. Coupling (mark G) | Nr | 2
7.62 | 355mm dia. Plain Ended Pipe 8m long (cut to suit on site) (mark H) | Nr | 1
7.63 | 355 mm dia Flange Adaptor | Nr | 1
7.64 | 355 mm dia. Blank Flange (mark J) | Nr | 1
7.65 | 355 x355mm dia. all Flanged Radial Tee (mark K) | Nr | 1
7.66 | 355mm dia. Flanged Spigot Pipe 1200mm long (mark L) | Nr | 1
7.67 | 355mm dia. Coupling (mark M) | Nr | 1
Overflow Ferrous Pipe Fittings to NP16 Details
7.68 | 150mm dia. Flanged Spigot Pipe 425mm long with a Puddle Flange at 162.5mm from the Spigot End (mark a) | Nr | 1
7.69 | 150mm dia. all Flanged 900 Bend (mark b) | Nr | 1
7.7 | 150mm dia. Flanged Spigot Pipe 439mm long (cut to suit on site) (mark c) | Nr | 1
7.71 | 150mm dia. Flange Adaptor (mark d) | Nr | 1
PAGE TOTAL CARRIED TO BILL COLLECTION SHEET
7.72 | 150mm dia. all Flanged 450 Bend (mark e) | Nr | 1
7.73 | 150mm dia. Flanged Spigot Pipe 502mm long with a Spigot End Bevelled (cut to suit on site) (mark f) | Nr | 1
Washout / Scour Ferrous Pipe Fittings to NP16 Details
7.74 | 150mm dia. Flanged Bellmouth (mark g) | Nr | 1
7.75 | 150mm dia. all Flanged 900 Bend (mark h) | Nr | 1
7.76 | 150mm dia. Double Flanged Pipe 2350mm long (mark i) | Nr | 1
7.77 | 150mm dia. all Flanged Gate Valve to BS 5163 (mark j) | Nr | 1
8 | VALVE CHAMBERS
8.1 | Provide all materials, excavate for and construct masonry inlet and outlet valve chambers, size 1200mm x 1200mm with precast cover slab and step irons. Depth n.e. 1.5m. | Nr | 2
8.2 | -Ditto - but masonry scour/overflow chamber size 1200mm x 1200mm . Depth n.e. 2.0m. | Nr | 1
9 | MISCELLANEOUS
9.1 | Allow a Provisional Sum of Kshs. 150,000 to be used as directed by the Engineer for any other Works as may be deemed necessary, e.g. Engineering Survey, Approval from relevant Authority for Road Works,etc. | Item | P.S
PAGE TOTAL CARRIED TO BILL COLLECTION SHEET

## Collection Sheet 5.1
TETU AGUTHI WATER SUPPLY PROJECT
BILL No. 5.1
BREAK PRESSURE TANKS 3NR (5m3)
Amount
Kshs.
Page Total, Page 1 of 7
Page Total, Page 2 of 7
Page Total, Page 3 of 7
Page Total, Page 4 of 7
Page Total, Page 5 of 7
Page Total, Page 6 of 7
Page Total, Page 7 of 7
Bill No. 5.1 Total Exclusive of VAT Carried to Section 5 Summary Sheet (3Nr)

## Asbestos Pipes
ASBESTOS PIPE REMOVAL, REPLACEMENT AND DISPOSAL
TETU RAW WATER GRAVITY MAIN LINE
Item | Description | Unit | Qty | Rate | Amount
CLASS A : GENERAL ITEMS
1 | Specified Requirements
Testing of the Works
Field Pressure Testing, Cleansing and Sterilisation of Pipelines
in Accordance with specifications
1.1 | Pressure Testing HDPE including all necessary equipment, materials and works necessary for testing, including transportation and use of water, pipe fittings, disposal of used water. | m | 15000
1.2 | Sterilization and Flushing as per specifications | m | 15000
Removal of Old Pipes
1.3 | Removal and Disposal of Asbstos pipes to an approved NEMA location in accordance with specifications of total length (15000m) | Ls | 1
CLASS D : DEMOLITION AND SITE CLEARANCE
1.4 | Clearance of Pipeline wayleave of shrubs, bushes and locally dispose nominal bore 250 mm | m | 15000
CLASS I : PIPEWORK - PIPES.
The rate quoted Is for supply, transport to site, setting out and pegging, laying and jointing of high density polyethylene (HDPE) pipes including backfilling of trenches, depth not exceeding 2 m. Include for preparation of trench surfaces; upholding sides of the excavation, disposal of excess excavated material, removal of dead services except to the extent that such work is included in classes J, K and L. All pipes of OD90 mm and above shall be jointed by Butt Fusion method.
HDPE Pipeline
1.5 | OD 250 mm HDPE PN16 | m | 15000
CLASS J : PIPEWORK - FITTINGS AND VALVES
Provision and installation of fittings and valves including excavation and backfilling of trenches, depth not exceeding 1.5m. Include for preparation of trench surfaces; upholding sides of the excavation, disposal of excess excavated material, removal of dead services except to the extent that such work is included in classes I, K and L
Class B uPVC pipes: Supply and transport pipes, break out surface, excavate trench, cut and lay pipes, backfill with selected material from the trench excavations and compact, disposal of surplus all as specified.
1.6 | Nominal bore 90 mm in trenches, depth not exceeding 1.5m | m | 30
HDPE Bends All sizes, PN 25
1.7 | Nominal Bore 250 mm PN20 (Provisional) | No | 10
Double Collars to PN16 as specified(Rate to include supply and fixing inclusive of Associated Fittings)
1.8 | Nominal bore 80mm x 90mm Viking Johnson stepped coupling | nr | 4
Adaptors (NP16)(Rate to include supply and fixing inclusive of Associated Fittings)
1.9 | Nominal bore 250 mm HDPE stub end with steel flange( for airvalves) | nr | 24
2 | Nominal bore 250 mm HDPE stub end with steel flange( for washouts) | nr | 8
2.1 | Nominal Bore 250 mm Mechanical Coupling | nr | 2
Straight Specials to PN16 Pressure as specified(Rate to include supply and fixing inclusive of Associated Fittings)
2.2 | Nominal bore 250mm diameter flanged spigot ferrous pipe, 1200mm long( for airvalves) | nr | 24
2.3 | Nominal bore 250mm diameter flanged spigot ferrous pipe, 1200mm long( for wash outs) | nr | 8
2.4 | Nominal bore 80mm plain ended ferrous pipe 1200mm long | nr | 4
Valves to PN 16 Pressure as specified(Rate to include supply and fixing inclusive of Associated Fittings)
2.5 | Nominal bore 50mm double flanged isolating Valve (for air valves) | nr | 12
2.6 | Nominal bore 80 mm double flanged Gate Valve (for washouts) | nr | 4
Air Valves to PN 16 Pressure as specified(Rate to include supply and fixing inclusive of Associated Fittings)
2.7 | Nominal bore 50 mm Vent-O-Matt RBX series or similar approved flanged double orifice air release and vacuum break valve | nr | 12
Air Valves and Washouts Fittings(Rate to include supply and fixing inclusive of Associated Fittings i.e. Mechanical Couplings, bolts and nuts etc.)
Junctions and Branches (NP16)(Rate to include supply and fixing inclusive of Associated Fittings)
2.8 | Nominal Bore 250mm x 200mm all flanged invert level tee (for Airvalve) | nr | 12
2.9 | Nominal Bore 200mm x 50 mm Reducer (For Airvalve) | nr | 12
3 | Nominal bore 250 mm x 200 mm all flanged ferrous invert level tee (for washouts) | nr | 4
3.1 | Nominal Bore 200mm x 80mm Reducer (For Washout) | nr | 4
CLASS K : PIPEWORK - MANHOLES, CHAMBERS AND
PIPEWORK ANCILLARIES
Construction of chambers as per drawings
3.2 | Chambers
3.2 | Ditto Airvalve chambers, depth 1.5 - 2m | nr | 12
3.3 | Ditto Washout chambers, depth 1.5 - 2m | nr | 4
BILL 1 TOTAL CARRIED TO SECTION COLLECTION SHEET