## REVISED GRAND SUMMARY
TANA WATER WORKS DEVELOPMENT AGENCY
KANYOKORA WATER SUPPLY PROJECT
GRAND SUMMARY
ORIGINAL
SECTION | DESCRIPTION |  | AMOUNT
(Kshs.)
1 | BILL No. 1.0 PRELIMINARIES AND GENERAL ITEMS
2 | BILL NO. 2.0 KAGIOINI - KANYOKORA RAW WATER GRAVITY MAIN LINE
3 | BILL NO 3.0 INTAKE WORKS
4 | Bills Total Exclusive of VAT | (A)
5% of A above
| Add …5%... of (A) for Contingencies | (B)
| Bill Total Inclusive of Contingencies - Exclusive of 16% V.A.T | (C)
| Value Added Tax (VAT) - 16% of (C) | (D)
GRAND TOTAL CARRIED TO LETTER OF BID [(C) + (D)]

## BIll No.1 PnG
KANYOKORA WATER SUPPLY PROJECT
BILL NO:1 | PRELIMINARIES AND GENERAL ITEMS
ITEM NO. | ITEM DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
CLASS A: GENERAL ITEMS
Contractual Requirements
A110 | Allow for Provision of Perfomance Bond in accordance with conditions of Contract | Item | Sum
A120 | Allow for Provision of Contractors All Risk Insurance in accordance with conditions of Contract. | Item | Sum
A130.1 | Allow for Provision of third party isurance (including employer's property) in accordance with conditions of contract | Item | Sum
A130.2 | Allow for Provision of Insurance against accidents to workmen | Item | Sum
Total Carried to Collection Sheet
Temporay Works
A26.1 | Test Running of the Works: Contractor to Test-run the newly constructed facilities for a period of 12 weeks upon completion of the Works including measurement and production of performance data (water quantity, quality etc.). Test Running to be carried out in close liaison with the Community Project Staff. The Contractor to allow for 'on job' training of Operation and Maintenance Staff, Tools, etc., and ensure that the operations are carried out full time on a 24 hour basis, all in accordance with Tender Document Specifications/Requirements. | Item | 1
A270 | Provide, erect and maintain (1 No) project sign board at the positions shown by the Engineer at site of works inclusive of removal and storage as directed by the Engineer at the end of the maintenance period. | No. | 1
A271 | Allow a P.C. Sum of Kshs. 450,000 for Payments demanded by the Authorities for relocation of existing services (water pipelines, power cable telcom cables etc) etc., including any statutory levies to relevant Authorities including KFS, NEMA and WRA. Liaison with the relevant Authorities shall be the responsibility of the Contractor for the timely execution of the Works. | 1 | Item
A272 | Add …….% for profit, administration, attendance upon, overheads, etc. for Item A271 above. | 7.5 | %
Method Related Charges
A311 | Provide for Contractors Campsite establishment and removal on completion. Mobilization and demobilization of equipment and personel and disposal of all waste material away from site as directed by the project Engineer. | Item | LS
A371.1 | Allow for Provisional Sum of Kshs. 1,200,000 to Cover the Cost of Employers Counterpart Staff attached to the Project | PC Item | 1
A371.2 | Allow a Provisional sum of Ksh. 120,000/month for Cost of Site meetings to be spent as instructed by the Engineer | Months | 6
A371.3 | Add % for profit, administration, attendance upon, overheads, etc. for Item A371.1- A371.2 above. | % | 0
A374 | Allow for production and provision of As-Built Drawings for all the works under the dedicated system in accordance with the General Conditions of Contract and Specifications/Requirements. | Item | 1
Provisional Sums
A410 | Allow a provisional sum of Kshs.100,000 for utilisation under schedule of dayworks for labour | Item | Sum
A412 | Add …….% for profit, administration, attendance upon, overheads, etc. for Item A410 above | % | 0
A413 | Allow a provisional sum of Kshs.50,000 for utilisation under schedule of dayworks for materials | Item | Sum
A414 | Add …….% for profit, administration, attendance upon, overheads, etc. for Item A413 above | % | 0
A420.1 | Allow a Provision Sum of Kshs. 250,000 for expenses related to Ground Breaking Ceremony and supply and installation of Project Plaque. Contractor to include for all requisite Works associated with installation. | Prov sum | 1
Total Carried to Collection Sheet
The Setting Out / Survey Work including establishment of Level Datum, production of Survey Drawings to an agreed scale will include the following:
A420.5 | Allow Provisional sum of Ksh 150,000 for Setting Out and Survey of the Works as directed by the Engineer in accordance with the General Conditions of Contract Document. | Item | 1
A420.6 | Add …….% for profit, administration, attendance upon, overheads, etc. for Item A420.5 above | % | 0
A420.7 | Allow a Provisional sum of Ksh 200,000 for any costs associated with compliance with Environmental, Health and Safety Requirements | Sum | L.S
Other Works
A420.8 | Provide all materials and construct concrete post and Chainlink fence as shown in the drawings. Height : 2.50 - 3.00 m | m | 90
A420.9 | Provide and install metal gate, width:3 m. | nr | 1
Total Carried Forward to Bill Collection Sheet
Page 1 Total
Page 2 Total
Page 3 Total
Grand Total Carried to Summary Page (exclusive of VAT)

## Bill No 2. Kagioini RWGM
TANA WATER WORKS DEVELOPMENT AGENCY
KANYOKORA WATER SUPPLY PROJECT
PIPE LINE.
BILL NO. 2.0 KAGIOINI - KANYOKORA RAW WATER GRAVITY MAIN LINE
Item | Description | Unit | Quantity | Rate | Amount
|  |  |  | (Kshs) | (Kshs)
A: GENERAL ITEM
A4.1.1 | Testing of works
A4.1.1.1 | Testing and Commissioning of the Pipeline including provision of all equipment, materials and works necessary for testing such as but not limited to Thrust Blocks, Anchor Blocks,Provision, Transportation and use and disposal of Water, Pipe Fittings,etc. | m | 4620.6
A4.1.1.2 | Disinfection of Pipeline ; Flushing with clear water, filling with water containing 0.05g/l Calcium Hypochlorite, left for 24 hours. This includes supply of necessary Equipment, Materials, Chemicals and Water, Measurement of Residual Chlorine, all as specified and safe disposal of disinfecting water to Engineer's approval. | m | 4620.6
A4.1.2 | Method Related Charges
The Pipeline will be laid along the road reserves where there is limited access and rural roads with existing active services both on the surface (electricity, etc) and buried (existing community water pipelines, fiber optic cables, etc.)
The Contractor's rates shall be deemed to include for any measures necessary to deal with these conditions, provision of access road to work site, liaison with relevant authorities and local residents, payment of any required statutory charges, etc. The Contractor will be required to submit Method Statement for execution of works under these specific conditions for approval prior to execution of the works. These include but are not limited to the following: i. No blasting will be permitted in these areas ii. The Contactor to maintain uninterrupted continuity of water supply in existing pipelines iii. Pedestrian and vehicular Access to individual shops / plots to be maintained at all times iv. Safety hoarding, lighting, bands, warning signs, etc. to be maintained at all times. v. Keeping trenches free of excessive groundwater, seepage or water from any source
A4.2.1.1 | Cost relating to the above mentioned specific conditions | Item | LS
A4.2.1.2 | Allow for a Provisional Sum of Kshs. 50,000 for liaison, facilitation with local residents and relevant authorities and payment for access, accidental damage, temporary access to working spaces during execution of the Works, etc. | Item | P.S
PAGE TOTAL CARRIED TO SECTION COLLECTION SHEET
CLASS D: DEMOLITION AND SITE CLEARANCE
D100 | Clear site for works as instructed 6m wide, including removal of trees and stumps with girths less than 0.5m, hedges, bushes and other vegetation or deleterious organic material, and back filling of holes left by removal of stumps and roots using approved material. | m | 4620.6
Tree Cutting (Provisional)
Cut down trees, grub up roots and cart away to tips
D210.1 | Girth: 0.5 m - 1.0 m | No | 30
CLASS E: EXCAVATION
Transport pipes from Site Store, Lay and fuse High Density Polyethylene (HDPE) Pipes in Trench,Nominal bore 180mm diameter as described, rates to include for Excavation, necessary trimming and alignment , Preparation of Surfaces, Disposal of Excavated Material, Shoring Sides of Excavation Trenches, Backfilling and Final Reinstatement. The pipes and fittings are to be laid in accordance with Drawings provided and to the Engineers instructions
E413 | OD 180-280mm in trench, depth not exceeding 1.0 m in soft/normal material | m3 | 2772.36
E414 | Ditto but depth 1m - 2 m | m3 | 1386.18
E425 | Extra over for excavation in hard material (Provisional) | m3 | 415.854
PAGE TOTAL CARRIED TO SECTION COLLECTION SHEET
CLASS I: PIPE WORK - PIPES
Supply, Transport to site and store in secure place. Include supply of jointing materials, bolts, nuts, gaskets, end caps etc as applicable Pipe dimensions/working pressures shall conform to ISO4427-2:2007 PE 100 Pipes.
I431.1 | Ditto but OD 280mm PN 16 | m | 459
I431.2 | Ditto but OD 280mm PN 12.5 | m | 520.2
I431.3 | Ditto but OD 180mm PN 12.5 | m | 3641.4
A-I7 | Double Flanged Steel Pipes- (Aerial River Crossings and Road Crosiings)
A-I72.1 | OD 280 mm, PN16 | m | 40
A-I72.2 | OD 180 mm, PN16 | m | 25
HDPE stub ends
A-I72.3 | OD 280mm HDPE stub ends with steel flange | No | 4
A-I72.4 | OD 180mm HDPE stub ends with steel flange | No | 2
CLASS J: PIPE WORK - FITTINGS AND VALVES
HDPE Fittings
Plain Ended Vertical /Horizontal Bends
J313.1 | Ditto but OD 180, 11.250 | No | 5
J313.2 | Ditto but 22.50 | No | 5
J313.3 | Ditto but 300 | No | 4
J313.4 | Ditto but 450 | No | 3
J313.5 | Ditto but 900 | No | 2
J313.5 | Ditto but OD 280, 11.250 | No | 3
J313.6 | Ditto but 22.50 | No | 2
J313.7 | Ditto but 300 | No | 2
J313.8 | Ditto but 450 | No | 1
PAGE TOTAL CARRIED TO SECTION COLLECTION SHEET
F2.2.3 | All Flanged Level Invert Tee (For Washouts)
F2.2.3.1 | OD 180 x OD 75mm | Nr | 3
F2.2.3.2 | OD 280 x OD 100mm | Nr | 1
HDPE Reducers, PN 25
J631.1 | Nominal bore 280 x180 mm | Nr | 1
Offtake to Kianjiru
F2.2.3.3 | OD 280 - 180mm HDPE PN16 Reducing tee | Nr | 1
F2.2.4 | Valves and Penstocks
F2.2.4.1 | All Flanged Gate Valves
Gate Valves for Washouts, Line Valves and isolation valves for Air Valves to be supplied complete with the spigot pipes, adapters, tees etc Contractor's rates to include for this and all necessary accessories
F2.2.4.1.1 | DN 180mm for LV | Nr | 4
F2.2.4.1.2 | DN 280mm FOR LV | Nr | 1
F2.2.4.1.3 | DN 80mm for WO | Nr | 5
F2.2.4.1.4 | DN 50mm for AV | Nr | 4
Air Valves
F2.2.4.2 | Double Orifice Air release valves to Specifications and Drawings
F2.2.4.2.1 | Nominal bore 50 mm , PN 20 | Nr | 4
CLASS K: PIPE WORK - CHAMBERS AND PIPEWORK ANCILLARIES
Chambers, ducts, culverts, crossings, thrust and anchor blocks, reinstatement and others as listed and specified in drawings.
Note:- Items for work in this class shall include:- - Excavation, preparation of surfaces, disposal of excavated material, shoring sides of excavation, backfilling and removal of redundant services. - Concrete, reinforcement, formwork, joints and finishes.
- Tips for disposal of excavated material or debris to be identified by the Contractor in liaison with the Local Authority.
IN SITU REINFORCED CONCRETE CHAMBERS
Provide all materials and construct Reinforced Concrete Chambers (Class 25/20), internal dimensions 1800mm x 1400mm. Include for supply and fixing of removable precast concrete covers, step irons, compacted granular fill, all formwork, etc. All as detailed on Drawing No. ..................
G2.2.1.2 | Depth 1.5 - 2.0m | Nr | 14
G2.2..3 | Method Related Charges
G2.2..3.2 | Allow for keeping excavation free of water which may occur through ground water seepage, rain or other means. | Item | L.S
G.2.2.5 | Other Pipework Ancillaries
G2.2.5.1 | Supply and fix marker posts along water Main Route, Road Crossings, change of direction, Air valves, Washouts and valve chambers. All in accordance with drawings and specifications as in Drawings | Nr | 38
G2.2.5.2 | Provide all materials and construct Masonry outfall structures on mass concrete plinths at washout drain pipe outlets. | Nr | 4
PAGE TOTAL CARRIED TO SECTION COLLECTION SHEET
H: PIPEWORK - SUPPORTS AND PROTECTION, ANCILLARIES TO LAYING AND EXCAVATION
H2.2 | Extra over excavation and backfilling for excavation in Rock. Rate to include carting away and disposal. (Provisional)
H2.2.1 | In Chambers
H2.2.1.1 | Excavation in trench for rock | m3 | 24.192
Crossings
River crossings, width not exceeding 30m, including 2No. HDPE Stub Flange Assembly With Adaptor, surrounds, bearings etc as per Drawings and to the Engineer's Approval. Rate to include for river diversion works and any other works necessary to be performed during and after construction of the crossing.
K622 | Over-crossing, pipe bore not exceeding 280mm as indicated in the Drawings. | Nr | 2
L7 | Concrete Support, Thrust Blocks, Stools/Slip Anchors and Anchor Blocks
Details as per Dwg No. (Provisional)
Rates to include for excavation, formwork, provision and placing of concrete, backfilling etc.
Class 20/20 Mass Concrete
NOTE:- The work includes pipe and fitting fixing
L71 | Volume not exceeding 0.1 m³
L71.1 | To pipes nominal bore not exceeding 280mm | Nr | 5
L72 | Volume:- 0.1 - 1m3
L72.1 | To pipes nominal bore not exceeding 280mm | Nr | 4
Class 25/20 Reinforced Concrete - For Anchor blocks
NOTE:- The work includes pipe and fitting fixing
L71 | Volume not exceeding 0.5 m³
L71.1 | To pipes nominal bore not exceeding 280mm | Nr | 1
L72 | Volume:- 0.5 - 2m3
L72.1 | To pipes nominal bore not exceeding 280mm | Nr | 10
Pipeline Piers and Supports as shown on drawing.
L8436.1 | Reinforced concrete pier complete with pipe cradle and strap, pier height not exceeding 4.0 - 6.0m. | Nr | 4
CLASS X:- MISCELLANEOUS WORKS
Open Cut Road Crossings
X61 | Provide all equipment and materials, open cut road surface in common material (soil/murram). The rate includes all preparatory works, any requisite shoring, strutting, installation of pipe and pipe casing, blanking of tunnel ends with mass concrete/masonry walls upon pipework installation, and necessary grouting and reinstatement, all in accordance with Drawings. Pipe nominal bore not exceeding 400mm. All works to be executed in close liaison with relevant road authorities and rates to include facilitation of the same. The Bidder to submit Method Statement with Bid for execution of these Works. | m | 15
PAGE TOTAL CARRIED TO SECTION COLLECTION SHEET
BILL SUMMARY SHEET
Page 1 Total
Page 2 Total
Page 3 Total
Page 4 Total
Page 5 Total
BILL TOTAL CARRIED TO GRAND SUMMARY

## Bill No 3.0 INTAKE
TANA WATER WORKS DEVELOPMENT AGENCY
KAGIOINI-KANYOKORA & KIANJIRU WATER SUPPLY PROJECT
BILL No. 3.0
INTAKE WORKS - INTAKE WEIR, INTAKE CHAMBER AND RIVER BED/BANK PROTECTION WORKS
ITEM | DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
No. |  |  |  | (Kshs) | (Kshs)
NOTE:
The Intake Works is located within Kirinyaga West Sub-County. The pipeline route is characterised with gentle slopes, vegetation and trees. The Contractor's rates should allow for any measures necessary to deal with the terrain, provision of access road to work sites, liason with the relevant authorities and local residents, obtaining permits for tree cutting, payments of any required statutory charges to Kenya Forest Service, etc. The costs for compliance shall be deemed to be coverd in the Contractor's rates.
A | GENERAL ITEMS
Temporary Works
2.2A275 | River diversion works at intake including construction of cofferdams, etc. Note: Bidder must submit proposed Method Statement for execution of these Works with the Bid. | Item | L.S
Method Related Charges
Specific conditions in execution of these Works are deemed to be included in the Contractor's rates. The Contractor will be required to submit Method Statement for execution of works under these specific conditions for approval prior to execution of the works. These include but are not limited to the following: i. No blasting will be permitted in these areas ii. Minimal disturbance of vegetation and trees including reistatement to original status after completion of the works. iv. Safety hoarding, lighting, bands, warning signs, etc. to be maintained at all times. v. Full time security from Kenya Forest Service Rangers during execution of the works
Method Related Charges for diversion of river and working in water logged area:
2.2A355 | Dewatering | Item | L.S
2.2A357 | Cofferdams | Item | L.S
2.2A380 | Any other method related charges the Bidder feels may be required. These should be indicated below in pricing of each item
i) | i) Allow a Provisional Sum of Kshs. 150,000/- for liaison, facilitation with local residents and relevant authorities and payment for access, accidental damage, temporary access to working spaces during execution of the Works, etc. | Item | P.S.
ii) | ……………………. | Item | L.S
ii) | ……………………. | Item | L.S
PAGE TOTAL CARRIED FORWARD TO COLLECTION PAGE
B | GROUND INVESTIGATIONS
Digging and Logging out of Trial Pit (1.0m x 1.0m) Along the Centerline of Intake Weir
2.2B111 | Depth n.e 1.0m | Nr | 1
2.2B112 | Depth 1 - 2m | Nr | 1
2.2B113 | Depth 2 - 3m | Nr | 1
D | DEMOLITION AND SITE CLEARANCE
Site Clearance of Entire Area of the Intake Works Site; Trees to be Cleared to be Identified by the Engineer: Rate to include for Carting Away and Disposing Cleared Material. Tips to be identified by the Contractor in liaison with Local Authority
2.2D100 | General clearance | ha | 0.04
2.2D210 | Trees of girth 500mm to 1m | Nr | 5
2.2D220 | Trees of girth 1m to 2m | Nr | 4
2.2D310 | Stumps of diameter 150mm to 500mm | Nr | 4
2.2D320 | Stumps of diameter 500mm to 1m | Nr | 3
E | EARTHWORKS
Excavations Shall Include for Strutting, Shuttering, Stabilizing Excavated Surfaces and Keeping Excavations Free of Water by Bailing Out, Pumping or Other Means
Excavation for Foundations
Intake Weir and Intake Chamber
2.2E311 | Topsoil depth n.e 0.25m | m3 | 40
2.2E321 | Material other than topsoil or rock depth 0.25 - 1.0m | m3 | 100
2.2E324 | Ditto but depth 1 - 2m | m3 | 150
2.2E325 | Ditto but depth 2 - 5m | m3 | 10
2.2E334 | Rock, depth 0.25 - 2m | m3 | 50
PAGE TOTAL CARRIED FORWARD TO COLLECTION PAGE
General Excavation
Improvement of Riverbed/Bank;
2.2E421 | Topsoil depth n.e 0.25m | m3 | 50
2.2E422 | Material other than topsoil or rock depth 0.25 - 1.0m | m3 | 150
2.2E423 | Ditto but depth 1 - 2m | m3 | 150
2.2E432 | Rock, depth n.e 0.25 -2m | m3 | 50
2.2E433 | Ditto but depth 2 - 5m | m3 | 50
Excavation Ancillaries
Trimming of Excavated Surfaces
2.2E512 | Material other than topsoil or rock | m2 | 200
2.2E513 | Trimming rock surfaces | m2 | 87
Disposal of Excavated Material
2.2E532 | Material other than top soil or rock | m3 | 300
2.2E533 | Rock | m3 | 150
Filling
Rates to include for compaction in 150mm layers as specified
2.2E614 | Selected Excavated material to intake chamber | m3 | 10
2.2E634 | General Filling on site using selected excavated material | m3 | 350
2.2E635 | General Filling on site using imported natural material other than top soil or rock | m3 | 150
F | IN SITU CONCRETE
Provision of Concrete
In situ Concrete
Mass Concrete
Bases
2.2F511 | C15 Blinding, 75mm thick | m3 | 15
2.2F512 | C15/20 Plum Concrete, 500mm thick (Provisional) | m3 | 30
PAGE TOTAL CARRIED FORWARD TO COLLECTION PAGE
Reinforced Concrete
Base Slabs
2.2F622 | C25 to Apron, Intake Chamber Base Slab and bases of Retaining Walls | m3 | 40
Suspended Slabs
2.2F632 | C25 to Roof Slab of Intake Chamber | m3 | 3
Walls
2.2F643 | C25 to Intake Chamber Walls and Retaining Walls | m3 | 25
Weir
2.2F680 | C25 to Weir Structure | m3 | 25
G | CONCRETE ANCILLARIES
Formwork - Rough finish
Plane Vertical to:-
2.2G144 | Foundation Keys | m2 | 40
2.2G145 | Buried faces of Retaining Walls and Intake Chamber Walls | m2 | 80
Formwork - Fair finish
Plane horizontal to:-
2.2G215 | Soffit of Intake Chamber Roof Slab | m2 | 20
Plane sloping to:-
2.2G225 | Weir - downstream face | m2 | 30
Plane Vertical to:-
2.2G245.1 | Weir - upstream face | m2 | 20
2.2G245.2 | Exposed faces of Retaining Walls and Intake Chamber Walls | m2 | 140
Curved to:-
2.2G254 | Weir Crest | m2 | 10
Rebates:-
2.2G286 | 50 x 50mm Rebates in Roof Slab of Intake Chamber for covers over openings | m | 15
PAGE TOTAL CARRIED FORWARD TO COLLECTION PAGE
Voids:-
2.2G271 | Small Voids in Intake Chamber Walls for Raw Water Pipe and Scour Pipe, depth n.e. 0.5m | Nr | 2
Reinforcement
Deformed High Yield steel bars to BS 4449
2.2G529 | High Yield Steel Bars, All sizes | Kg | 12090
Concrete Accessories
Finishing of Top Surfaces
2.2G812 | Steel Trowel finish to top surface of Apron and base of Intake Chamber | m2 | 100
Inserts - Rate to Include for Supply and Fixing in Concrete
Ferrous Pipes Coated externally or Approved equivalent and Cement Mortar lined internally pipes - PN 16
2.2G831.1 | DN 180 steel plain ended pipe piece for Raw Water Outlet, length n.e 30m, projecting from one surface of Intake Chamber Wall, and with puddle flange at 225mm from one end. | Nr | 1 |  |  | 0.66667 | 24000
2.2G831.2 | DN 90 steel plain ended pipe piece for Scour, length n.e 8.0m, projecting from one surface of Intake Chamber Wall, and with puddle flange at 225mm from one end and all associated fittings | Nr | 1
I | PIPEWORK - PIPES
Provide and lay pipes in trenches
Raw Water Gravity Main and Scour Pipeline Within Intake Works Site - Approved Lines Ferrous Pipes
2.2I415 | DN 90 in trenches depth n.e 3.0m. | m | 20
2.2I435 | DN 280 in trenches depth n.e 3.0m. | m | 15 |  |  | 7441.3333
J | PIPEWORK - FITTINGS AND VALVES
Rates to include for provision and fixing.
Flexible Coupling
2.2J341 | DN 90 | Nr | 1
2.2J343 | DN 280 | Nr | 2 |  |  | 12314
PN16 Double Flanged Sluice Valves complete with fittings (As type AVK - Denmark or similar equivalent)
2.2J344 | DN 90 | Nr | 1
2.2J345 | DN 280 | Nr | 1
Penstocks - Hand Operated
2.2J882 | DN 280 with extension spindle, guide brackets, headstock and hand wheel | Nr | 1 |  |  | 159949.3333
PAGE TOTAL CARRIED FORWARD TO COLLECTION PAGE
N | MISCELLANEOUS METALWORK
2.2N140 | GMS Guardrails, 0.9m high as per detail on Drg | m | 24
2.2N162 | GMS Fine Screen Guides, made of 60x50x5mm Channel Sections as per detail on Drg. | m | 10
2.2N180 | GMS Open Grating Flooring over access opening for Fine Screens, made of 20mm dia bars welded to 45x45x4mm GMS Angle Frame, size 900mm x 690mm, as per detail on Drg. | Nr | 3
2.2N230 | GMS Lockable Covers size 670mm x 670mm for 600mm x 600mm clear manhole openings in roof of Intake Chamber as per detail on Drg | Nr | 2
2.2N299.1 | GMS Plate, size 125x100x5mm thick, welded to Fine Screen Guide Channels and fixed to concrete walls with 1 Nr 12mm dia Rawl Bolt, 100mm long, (rate to include for the bolts, welding to fine screen guide and fixing to concrete wall) all as per details on Drg. | Nr | 42
2.2N299.2 | GMS Locking Bars for Manhole Covers, size 850x50x6mm thick as per details on Drg. | Nr | 5
2.2N299.3 | Cast Iron Step Irons fixed to wall of Intake Chamber | Nr | 10
2.2N299.4 | GMS Coarse Screen, size 1600x1300mm, fabricated using GMS bars, dia 20 mm at spacing 40 mm welded to frame fixed with fish tailed lugs into concrete walls, all as per details on Drg | Nr | 1
2.2N299.5 | GMS Fine Screens, size 2475mm x 560mm, fabricated using 10mm dia M.S. bars at 10mm spacing and 3mm thick plate with 4mm dia. holes, with GMS frame and lifting handles, all as per details on Drg | Nr | 2
X | RIVER BED AND BANK PROTECTION WORKS
Rock Filled Gabions
2.2X410 | Box Gabions, size 2m x 1m x 1m, mesh wire 2.0mm diameter, laid in stretches with 0.5m overlap, filled with approved hardcore. | Nr | 20
2.2X420 | Gabion Matresses, thickness 500mm, mesh wire 2.0mm diameter, filled with approved hardcore. | m2 | 40
PAGE TOTAL CARRIED FORWARD TO COLLECTION PAGE

## Intake Collection Sheet
TANA WATER WORKS DEVELOPMENT AGENCY
KANYOKORA WATER SUPPLY PROJECT
INTAKE - COLLECTION SHEET
Amount
(Kshs)
Page Total, Page 1 of 6
Page Total, Page 2 of 6
Page Total, Page 3 of 6
Page Total, Page 4 of 6
Page Total, Page 5 of 6
Page Total, Page 6 of 6
Bill No. 4 Total Exclusive of VAT Carried to Summary Sheet